## Sheet1
Chilled Water Reset
Return Reset |  |  |  | Outdoor Reset
| Outdoor Air Temperature> | >>>>>>>>>>>>>>>>>>>>> |  | 40 | °F
| Chilled water setpoint> |  | °F | 45 | °F
| enter Reset ratio> |  | % | 0 | %
| enter Start Reset > |  | °F | 50 | °F
| Leaving water temp> |  | °F
| Entering water temp> |  | °F
| New Chilled Water Set Point> | 0 | °F | 45 | °F
reset type | reset ratio range | start reset range |  | maximum reset range |  | increment | facrtory default
return | 10% to 120% | 4°F to 30°F |  | 0°F to 20°F |  | 1% | 50%
outdoor | 80% to -80% | 50°F to 130°F |  | 0°F to 20°F |  | 1% | 10%