|  | - Reference Material |
| --- | --- |
|  | - TR150 Programming Guide BAS-SVP16A-EN |
|  | - Customer Connection Diagram (specific for the order). |
|  | - Schematic Diagram (specific for the order). |
|  | - Pre-Installation Checks |
|  | - Compare the drive model number to what was ordered. |
|  | - Be sure the following are for the same voltage: |
|  | - Drive. |
|  | - Power line. |
|  | - Motor. |
|  | - Record the following motor data: |
|  | - Voltage |
|  | - Frequency |
|  | - Full load current |
|  | - Full load speed |
|  | - Power |
|  | - Be sure that rated drive current is greater than or equal to the total full load current of all motors which will be driven at once. |
|  | - Check motor wiring: |
|  | - A disconnect or contactor between the drive and the motor may need to be interlocked to the drive or else nuisance trips may occur. |
|  | - Multiple motors have individual motor overload and short circuit protection. |
|  | - No power factor correction capacitors between the drive and the motor. |
|  | - Two speed motors must be wired permanently for full speed. |
|  | - Y-start, ∆-run motors must be wired permanently for run. |
|  | - Part winding start motors must be wired permanently for run. |
|  | - Installation Checks |
|  | - Verify appropriate short circuit protection is provided at the input of the drive. Specific fuse requirement necessary for UL (see instruction manual) |
|  | - Measure phase to phase line voltage and ensure measured voltage is within drive specification (see instruction manual) |
|  | - Measure phase to ground voltage. If any measured phase voltage is greater than 60% of phase to phase voltage, open RFI switch. |
|  | - Environmental concerns. |
|  | - Suitable for drive enclosure type, Chassis, NEMA/UL Type 1, 12, 3R or 4 |
|  | - Max 95% relative humidity, non-condensing. |
|  | - 14oF to 113oF ambient temperature range (typical). |
|  | - 3300 foot maximum elevation with no de-rating. |
|  | - Non-corrosive environment or unit conformal coated. |
|  | - Mounting |
|  | - No heat sink fins exposed out the back. |
|  | - Drive mounting clearances observed (see instruction manual) |
|  | - No excessive vibration. |
|  | - Keep dirt and debris out of the drive |
|  | - Use knock-outs provided or conduit entry plates for wire entry |
|  | - Connections and Wiring |
|  | - Check all wiring connections are secure. |
|  | - Each drive grounded individually, no daisy chain grounds. |
|  | - 0-10Vdc and ma signal wires protected from noise. |
|  | - Separated runs for input power, motor power, and control wiring. |
|  | - Note some control connections may be 115VAC. |
|  | - Motor thermistor wires separate from load wires. |
|  | - Powering Drive |
|  | - Double check all wire connections (correct terminal connection, correct tightness) |
|  | - All RUN commands off, all speed commands set to zero. |
|  | - Switch Power on. |
|  | d. Display and PWR LED on. |
|  | - Basic Drive Set-up, Use Main Menu — THIS STEP IS ESSENTIAL!!! |
|  | - Parameter 0-03, REGION NORTH AMERICAN |
|  | - Parameter 1-03, TORQUE CHARACTERISTICS (AUTO ENERGY OPTIM. VT for BELT DRIVE FANS VARIABLE TORQUE for DIRECT DRIVE PLENUM FANS ONLY) |
|  | - Parameter 1-20, MOTOR POWER (HP) BASED ON UNIT NAMEPLATE DATA |
|  | - Parameter 1-22, MOTOR VOLTAGE (V) BASED ON UNIT NAMEPLATE DATA |
|  | - Parameter 1-24, MOTOR CURRENT (A) REFER TO UNIT NAMEPLATE DATA |
|  | - Parameter 1-25, MOTOR NOMINAL SPEED (RPM) REFER TO MOTOR NAMEPLATE |
|  | - Parameter 1-71, START DELAY (SEC) 2 SEC |
|  | - Parameter 1-73, FLYING START, ENABLE |
|  | - Parameter 1-90, MOTOR THERMAL PROTECTION, ETR TRIP 1 [4] |
|  | - Parameter 3-02, MINUMUM REFERENCE (HZ) 0HZ |
|  | - Parameter 3-03, MAXIMUM REFERENCE (HZ) REFER TO UNIT NAMEPLATE DATA |
|  | - Parameter 3-15, TERMINAL 53 ANALOG INPUT, ANALOG INPUT 53 |
|  | - Parameter 3-41, RAMP-UP TIME (SEC.) 30 SEC |
|  | - Parameter 3-42, RAMP-DOWN TIME (SEC) 30 SEC |
|  | - Parameter 4-12, OUTPUT FREQ LOW LIMIT (HZ) 20HZ |
|  | - Parameter 4-14, OUTPUT FREQ HIGH LIMIT (HZ) REFER TO UNIT NAMEPLATE DATA |
|  | - Parameter 4-18, CURRENT LIMIT %, 110% |
|  | - Parameter 4-19, MAX OUPUT FREQ (HZ) REFER TO UNIT NAMEPLATE DATA |
|  | - Parameter 5-12, TERMINAL 27 DIG. INPUT, COAST INVERSE |
|  | - Parameter 5-40, FUNCTION RELAY, RELAY 1 ACTIVE NO ALARM[160] RELAY 2 ACTIVE MOTOR RUNNING [5] |
|  | - Parameter 6-14, TERMINAL 53 LOW REF FEEDBACK (HZ) 20HZ |
|  | - Parameter 6-15, TERMINAL 53 HIGH REF FEEDBACK (HZ) REFER TO UNIT NAMEPLATE DATA |
|  | - Parameter 14-01, SWITCHING FREQ (KHZ) SET TO MAX FOR HP REFERENCE TABLE 37 |
|  | - Parameter 14-20, RESET MODE, AUTOMATIC RESET x 5 |
|  | - Parameter 1-29, AUTOMATIC MOTOR ADAPTATION |
|  | - Operational Tests — HAND |
|  | - Check the motor’s rotation from the drive. If incorrect, reverse two leads between the drive and the motor. |
|  | - If a bypass is provided, check the motor’s rotation in bypass mode. If incorrect, reverse two input power lines. |
|  | - Accelerate the motor to full speed and verify operation. |
|  | - Decelerate the motor to a stop and verify operation. |
|  | - Operational Tests — AUTO, Open Loop |
|  | - Ensure that the drive follows run/stop commands from the system. |
|  | - Ensure that the drive follows the speed command from the system. |
|  | - Set final MIN/MAX References as required – Parameters 3-02 and 3-03 |
|  | - Set final RAMP UP/RAMP DOWN Times as required – Parameters 3-41 and 3-42 |
|  | - Operational Tests — Auto, Closed Loop |
|  | - Set up the PID control parameters as required. |
|  | - Ensure that the drive follows run/stop commands from the system. |
|  | - Ensure that the drive responds to the feedback signal from the system. |
|  | - Final Adjustments |
|  | - Copy parameters to other setups as required, Parameter 0-51 - Copy parameters to the LCP, Parameter 0-50 |