## Low Oil Flow
Directions: Enter Condenser Pressure, Intermediate Oil Pressure, and Evaporator Pressure. Results indicate Oil Pressure drop; and Oil Filter Life. | [12 empty] | Oil Flow Forcing DP | OPD operating < 2.5 minutes | OPD operating > 2.5 minutes | Dirty Filter
| Note: Condensing Pressure will always be greater than the intermediate oil pressure. ( Deffinition: OPD = Oil Pressure Drop ) | [11 empty] | 4 | 220.2 | 180.2 | 158
Condenser/Discharge Pressure |  | Pc = | 80 | psig | [8 empty] | 5 | 200.1912 | 163.3584 | 143.2698
Intermediate Oil Pressure |  | Pi = | 60 | psig | [6 empty] | Scroll down to see PLOT of Oil Filter Life |  | 6 | 185.4344 | 150.9395 | 132.4095
Evaporator Pressure |  | Pe = | 40 | psig | [8 empty] | 7 | 173.9765 | 141.2986 | 123.9801
[13 empty] | 8 | 164.7503 | 133.5371 | 117.1949
Oil Flow Forcing DPcktx = PCond_cktx - ( 1.5 * PEvap_cktx ) | [5 empty] | = | 20 | psi |  |  |  | 20 | 9 | 157.1167 | 127.1167 | 111.5833
| This value shall be clamped to never be less than 4 psid. | [11 empty] | 10 | 150.6666 | 121.6929 | 106.8438
[13 empty] | 11 | 145.1243 | 117.0336 | 102.7732
Oil Pressure Dropcktx = PCond_cktx - Pintermediate_oil_cktx | [5 empty] | = | 20 | psi |  |  |  | 100 | 12 | 140.2966 | 112.976 | 99.229
[13 empty] | 13 | 136.043 | 109.402 | 96.108
Oil_Pressure_Drop_Ratiocktx = SqRoot ( Oil_Pressure_Dropcktx / Oil_Flow_Forcing_DPcktx ) | [8 empty] | = | 1 |  |  | 14 | 132.2593 | 106.2236 | 93.3331
[13 empty] | 15 | 128.8656 | 103.3736 | 90.8457
[13 empty] | 16 | 125.8 | 100.8 | 88.6
System Differential above 15 psid: | [12 empty] | 17 | 123.0135 | 98.4614 | 86.56
For the first 2.5 minutes; Start-up: |  |  | Calculation: Acceptable_Oil_Pressure_Drop_Ratio < 0.3 + (.0005 * Oil_Flow_Forcing_DPcktx ) + ( 3.8 / SqRoot(Oil_Flow_Forcing_DPcktx)) | [9 empty] | 18 | 120.4669 | 96.3247 | 84.6966
[13 empty] | 19 | 118.128 | 94.363 | 82.9864
|  |  |  | First 2.5 minutes Result: | 1 | < | 1.1597 |  |  |  | Oil Pressure Drop ACCEPTABLE |  | 20 | 115.9706 | 92.5542 | 81.4099
[13 empty] | 21 | 113.9728 | 90.8797 | 79.951
and thereafter; Running: |  |  | Calculation: Acceptable_Oil_Pressure_Drop_Ratio < 0.2 + (.0005 * Oil_Flow_Forcing_DPcktx ) + ( 3.2 / SqRoot(Oil_Flow_Forcing_DPcktx)) | [9 empty] | 22 | 112.1163 | 89.3242 | 78.5962
[13 empty] | 23 | 110.3855 | 87.8746 | 77.334
|  |  |  | After 2.5 minutes Result: | 1 | < | 0.92554 |  |  |  | Oil Pressure Drop NOT ACCEPTABLE |  | 24 | 108.7672 | 86.5197 | 76.1548
[13 empty] | 25 | 107.25 | 85.25 | 75.05
[13 empty] | 26 | 105.8241 | 84.0572 | 74.0125
Dirty Filter Trip Point (for current conditions): 0.12 + 0.058 + ( 0.0005 * Oil_Flow_Forcing_DPcktx) + ( 2.8 / SqRoot (Oil_Flow_Forcing_DPcktx )) | [11 empty] | 0.8141 | 27 | 104.481 | 82.934 | 73.036
[13 empty] | 28 | 103.2132 | 81.8743 | 72.115
Oil Filter Life Remaining: |  |  |  |  | 0 | % | [5 empty] | -154.9175 | 29 | 102.0142 | 80.8725 | 71.2447
[13 empty] | 30 | 100.8782 | 79.9237 | 70.4208
[13 empty] | 31 | 99.8 | 79.0237 | 69.6395
[13 empty] | 32 | 98.7751 | 78.1685 | 68.8975
[13 empty] | 33 | 97.7995 | 77.3548 | 68.1917
[13 empty] | 34 | 96.8695 | 76.5795 | 67.5196
[13 empty] | 35 | 95.9817 | 75.8399 | 66.8786
[13 empty] | 36 | 95.1333 | 75.1333 | 66.2667
[13 empty] | 37 | 94.3216 | 74.4577 | 65.6817
[13 empty] | 38 | 93.5441 | 73.8109 | 65.122
[13 empty] | 39 | 92.7987 | 73.191 | 64.5859
[13 empty] | 40 | 92.0833 | 72.5964 | 64.0719
[13 empty] | 41 | 91.396 | 72.0256 | 63.5787
[13 empty] | 42 | 90.7353 | 71.4771 | 63.1049
[13 empty] | 43 | 90.0995 | 70.9495 | 62.6496
[13 empty] | 44 | 89.4872 | 70.4418 | 62.2116
[13 empty] | 45 | 88.8971 | 69.9528 | 61.7899
[13 empty] | 46 | 88.3279 | 69.4814 | 61.3837
[13 empty] | 47 | 87.7787 | 69.0268 | 60.9922
[13 empty] | 48 | 87.2483 | 68.588 | 60.6145
[13 empty] | 49 | 86.7357 | 68.1643 | 60.25
[13 empty] | 50 | 86.2401 | 67.7548 | 59.898
[13 empty] | 51 | 85.7606 | 67.359 | 59.5578
[13 empty] | 52 | 85.2965 | 66.976 | 59.229
[13 empty] | 53 | 84.847 | 66.6054 | 58.911
[13 empty] | 54 | 84.4115 | 66.2465 | 58.6032
[13 empty] | 55 | 83.9892 | 65.8988 | 58.3052
[13 empty] | 56 | 83.5796 | 65.5618 | 58.0166
[13 empty] | 57 | 83.1822 | 65.235 | 57.7369
[13 empty] | 58 | 82.7964 | 64.9181 | 57.4658
[13 empty] | 59 | 82.4218 | 64.6105 | 57.2029
[13 empty] | 60 | 82.0578 | 64.3118 | 56.9478
[13 empty] | 61 | 81.704 | 64.0218 | 56.7003
[13 empty] | 62 | 81.36 | 63.74 | 56.46
[13 empty] | 63 | 81.0255 | 63.4662 | 56.2267
[13 empty] | 64 | 80.7 | 63.2 | 56
[13 empty] | 65 | 80.3832 | 62.9411 | 55.7797
[13 empty] | 66 | 80.0748 | 62.6893 | 55.5656
[13 empty] | 67 | 79.7744 | 62.4442 | 55.3574
[13 empty] | 68 | 79.4818 | 62.2057 | 55.155
[13 empty] | 69 | 79.1966 | 61.9735 | 54.958
[13 empty] | 70 | 78.9187 | 61.7473 | 54.7664
[13 empty] | 71 | 78.6477 | 61.527 | 54.5799
[13 empty] | 72 | 78.3834 | 61.3124 | 54.3983
[13 empty] | 73 | 78.1256 | 61.1032 | 54.2215
[13 empty] | 74 | 77.8741 | 60.8992 | 54.0493
[13 empty] | 75 | 77.6286 | 60.7004 | 53.8816
[13 empty] | 76 | 77.389 | 60.5065 | 53.7182
[13 empty] | 77 | 77.155 | 60.3174 | 53.559
[13 empty] | 78 | 76.9265 | 60.1329 | 53.4038
[13 empty] | 79 | 76.7033 | 59.9528 | 53.2525
[13 empty] | 80 | 76.4853 | 59.7771 | 53.105
[13 empty] | 81 | 76.2722 | 59.6056 | 52.9611
[13 empty] | 82 | 76.064 | 59.4381 | 52.8208
[13 empty] | 83 | 75.8604 | 59.2746 | 52.684
[13 empty] | 84 | 75.6614 | 59.1149 | 52.5505
[13 empty] | 85 | 75.4668 | 58.9589 | 52.4203
[13 empty] | 86 | 75.2765 | 58.8065 | 52.2932
[13 empty] | 87 | 75.0903 | 58.6576 | 52.1692
[13 empty] | 88 | 74.9081 | 58.5121 | 52.0481
[13 empty] | 89 | 74.7299 | 58.3699 | 51.9299
[13 empty] | 90 | 74.5555 | 58.231 | 51.8146
[13 empty] | 91 | 74.3848 | 58.0951 | 51.702
[13 empty] | 92 | 74.2177 | 57.9623 | 51.592
[13 empty] | 93 | 74.0542 | 57.8325 | 51.4846
[13 empty] | 94 | 73.894 | 57.7055 | 51.3798
[13 empty] | 95 | 73.7372 | 57.5813 | 51.2774
[13 empty] | 96 | 73.5836 | 57.4599 | 51.1774
[13 empty] | 97 | 73.4332 | 57.3411 | 51.0797
[13 empty] | 98 | 73.2858 | 57.2249 | 50.9843
[13 empty] | 99 | 73.1414 | 57.1112 | 50.8911
[13 empty] | 100 | 73 | 57 | 50.8
[13 empty] | 101 | 72.8614 | 56.8912 | 50.711
[13 empty] | 102 | 72.7256 | 56.7847 | 50.6241
[13 empty] | 103 | 72.5925 | 56.6805 | 50.5392
[13 empty] | 104 | 72.4621 | 56.5786 | 50.4563
[13 empty] | 105 | 72.3342 | 56.4788 | 50.3752
[13 empty] | 106 | 72.2089 | 56.3811 | 50.296
[13 empty] | 107 | 72.086 | 56.2856 | 50.2186
[13 empty] | 108 | 71.9655 | 56.192 | 50.143
[13 empty] | 109 | 71.8474 | 56.1004 | 50.0691
[13 empty] | 110 | 71.7316 | 56.0108 | 49.997
[13 empty] | 111 | 71.618 | 55.9231 | 49.9264
[13 empty] | 112 | 71.5066 | 55.8372 | 49.8575
[13 empty] | 113 | 71.3974 | 55.7531 | 49.7902
[13 empty] | 114 | 71.2903 | 55.6707 | 49.7244
[13 empty] | 115 | 71.1852 | 55.5902 | 49.6601
[13 empty] | 116 | 71.0821 | 55.5113 | 49.5973
[13 empty] | 117 | 70.981 | 55.434 | 49.536
[13 empty] | 118 | 70.8818 | 55.3584 | 49.4761
[13 empty] | 119 | 70.7845 | 55.2844 | 49.4176
[13 empty] | 120 | 70.6891 | 55.2119 | 49.3604
[13 empty] | 121 | 70.5955 | 55.1409 | 49.3045
[13 empty] | 122 | 70.5036 | 55.0714 | 49.25
[13 empty] | 123 | 70.4134 | 55.0034 | 49.1967
[13 empty] | 124 | 70.325 | 54.9368 | 49.1447
[13 empty] | 125 | 70.2382 | 54.8717 | 49.094
[13 empty] | 126 | 70.1531 | 54.8079 | 49.0444
[13 empty] | 127 | 70.0695 | 54.7454 | 48.996
[13 empty] | 128 | 69.9876 | 54.6843 | 48.9487
[13 empty] | 129 | 69.9071 | 54.6244 | 48.9026
[13 empty] | 130 | 69.8282 | 54.5659 | 48.8576
[13 empty] | 131 | 69.7508 | 54.5085 | 48.8137
[13 empty] | 132 | 69.6748 | 54.4524 | 48.7709
[13 empty] | 133 | 69.6002 | 54.3975 | 48.7291
[13 empty] | 134 | 69.527 | 54.3438 | 48.6883
[13 empty] | 135 | 69.4552 | 54.2912 | 48.6486
[13 empty] | 136 | 69.3847 | 54.2398 | 48.6098
[13 empty] | 137 | 69.3156 | 54.1894 | 48.572
[13 empty] | 138 | 69.2477 | 54.1402 | 48.5352
[13 empty] | 139 | 69.1812 | 54.092 | 48.4993
[13 empty] | 140 | 69.1159 | 54.0449 | 48.4643
[13 empty] | 141 | 69.0518 | 53.9989 | 48.4303
[13 empty] | 142 | 68.9889 | 53.9538 | 48.3971
[13 empty] | 143 | 68.9272 | 53.9097 | 48.3648
[13 empty] | 144 | 68.8667 | 53.8667 | 48.3333
[13 empty] | 145 | 68.8073 | 53.8246 | 48.3027
[13 empty] | 146 | 68.749 | 53.7834 | 48.273
[13 empty] | 147 | 68.6919 | 53.7432 | 48.244
[13 empty] | 148 | 68.6358 | 53.7038 | 48.2159
[13 empty] | 149 | 68.5808 | 53.6654 | 48.1885
[13 empty] | 150 | 68.5269 | 53.6279 | 48.1619
[13 empty] | 151 | 68.474 | 53.5912 | 48.1361
[13 empty] | 152 | 68.4221 | 53.5554 | 48.111
[13 empty] | 153 | 68.3712 | 53.5205 | 48.0867
[13 empty] | 154 | 68.3213 | 53.4863 | 48.063
[13 empty] | 155 | 68.2723 | 53.453 | 48.0401
[13 empty] | 156 | 68.2243 | 53.4205 | 48.0179
[13 empty] | 157 | 68.1773 | 53.3888 | 47.9964
[13 empty] | 158 | 68.1312 | 53.3578 | 47.9756
[13 empty] | 159 | 68.086 | 53.3277 | 47.9554
[13 empty] | 160 | 68.0416 | 53.2982 | 47.9359
[13 empty] | 161 | 67.9982 | 53.2695 | 47.9171
[13 empty] | 162 | 67.9556 | 53.2416 | 47.8989
[13 empty] | 163 | 67.9139 | 53.2143 | 47.8813
[13 empty] | 164 | 67.873 | 53.1878 | 47.8643
[13 empty] | 165 | 67.833 | 53.162 | 47.848
[13 empty] | 166 | 67.7937 | 53.1368 | 47.8322
[13 empty] | 167 | 67.7553 | 53.1123 | 47.8171
[13 empty] | 168 | 67.7176 | 53.0885 | 47.8025
[13 empty] | 169 | 67.6808 | 53.0654 | 47.7885
[13 empty] | 170 | 67.6447 | 53.0429 | 47.775
[13 empty] | 171 | 67.6093 | 53.021 | 47.7621
[13 empty] | 172 | 67.5747 | 52.9998 | 47.7498
[13 empty] | 173 | 67.5409 | 52.9791 | 47.738
[13 empty] | 174 | 67.5077 | 52.9591 | 47.7267
[13 empty] | 175 | 67.4753 | 52.9397 | 47.716
[13 empty] | 176 | 67.4436 | 52.9209 | 47.7058
[13 empty] | 177 | 67.4125 | 52.9027 | 47.6961
[13 empty] | 178 | 67.3822 | 52.885 | 47.6869
[13 empty] | 179 | 67.3525 | 52.8679 | 47.6782
[13 empty] | 180 | 67.3235 | 52.8514 | 47.67
Note on Q2: Larry Volk: Column P, Q, R, S, T, U…hidden calculations and graphing information. To unHide edit General Format.

## Notes
Acceptable_Oil_Pressure_Drop_Ratio < 0.3 + (.0005 * Oil_Flow_Forcing_DPcktx ) + ( 3.8 / SqRoot(Oil_Flow_Forcing_DPcktx))
Acceptable_Oil_Pressure_Drop_Ratio < 0.2 + (.0005 * Oil_Flow_Forcing_DPcktx ) + ( 3.2 / SqRoot(Oil_Flow_Forcing_DPcktx))
From the functional specification:
System Differential above 23psid:
For the first 2.5 minutes: |  | 0.50 > (Pc - Po) / (Pc - Pe)
and thereafter: |  | 0.40 > (Pc - Po) / (Pc - Pe)
System Differential below 23psid:
For the first 2.5 minutes: |  | 0.60 > (Pc - Po) / (Pc - Pe)
and thereafter: |  | 0.50 > (Pc - Po) / (Pc - Pe)
Reference:
IF( condition1, value_if_true1, IF( condition2, value_if_true2, value_if_false2 ))
Oil Forcing DP (Pc-Pe*1.5)
% of Oil Pressure Drop