## Known Issues
Product | Problem | Solution | Change Request | Service Bulletin | POC
BCXD | Floating Actuator will not open | Wire harness 501998770200 is used instead of the 0100 extension | Yes | Yes | Mark
BCXD | L1 and N swapped | Black is L1, White is neutral. Does not matter since this is AC voltage per EE
VUVE | DX, EH, CSTI. DX does not work. | 1TB3-7 is not the DX input on board. Use 1TB3-6 for field wiring | Yes | ?? | David
VUVE | DX circuit harness built wrong (650 Units) | Reverse two wires??? See Dan Gochenaur (waiting for serial numbers) | ? | Yes | Kevin

## VUVE
2-10v F&B damper actuator | X13611409020
Floating point F&B Damper Actuator | X13611407010
3 pos fan speed switch used on HUVC | x13460098010
3/4 x 3/4 black insulation for back of unit | x21130611010 | x23010119100 (new, possibly 07/11/2007) |  | X13611011020 HAS BECOME OBSOLETE.
Aux drain pan Brackets; Left side |  | BRK03675 | 4619 – 1092 – 0100
Aux drain pan Brackets; Right side |  | BRK03553 | 4619 – 1093 – 0100
Aux Drain Pan | X20600650010 | PAN02740
Black clip for hex head speed screw for access door | x28020282010 | CLP01049
Black Hex Head Speed screw for access door | x25020250010 | SCR02132
black ring for access door | x32170012010 |  |  | PARENT PARTS:
clip for freezestat on Horizonal units | x32030058010
Condensate / Rubber / P-Trap Hose from bottom of pan |  | TUB11616
Description | X Code | CATS | 4619
Discharge Air Steel Grille - 075 |  | GRL01543
Discharge Air Steel Grille - 100 |  | GRL01544
Discharge Air Steel Grille - 125 |  | GRL01545
Discharge Air Steel Grille - 150 |  | GRL01546
Discharge Air Thermistor for F&B (black serpentine) | x13790124010 | SEN00484
End Panel mounting hardware (4 parts required per panel)
F&B Block off | 4619-0415 |  |  | 0100-750cfm | 0200-1000cfm | 0300-1250cfm | 0400-1500cfm
Fan Status Sensor (Hawkeye 800) | X13470536010 | SWT02336
Freeze stat | X13100276030 | CNT01847 |  | 461911450200 (COILB-FB 2-10V ACTUATOR)
Frost stat | X13100276090 | CNT03049
GASKET; .75 X .75 X 20 FOOT ROLL | X23010119-10-0 | GKT04114 |  | For back of unit to seal the unit to the wall.
Hardware assembly for end plates is = HARDWARE;END COVER MNTG | 461916730100 Baggie
Hex head screw for access panels 1.25 inch | x25020250010
Honeywell 0-10v Actuator- For water valves VC7930 |  | ACT00486 |  | New capacitors are installed in date code 0814 or later changed 3/24/08
Label sheet with all the labels | X39001531050
New F&B Damper Assy for 750 size unit | 461915250100 | KIT14803
New F&B Damper Assy for 1000 size unit | 461915250200 | KIT14804
New F&B Damper Assy for 1250 size unit | 461915250300 | KIT14805
New F&B Damper Assy for 1500 size unit | 461915250400 | KIT14806
Nut | X28022700000
OA/ RA ACTUATOR;BELIMO 2-10V O/A | X13611002040 | ACT00340 |  | The CN: UV5134 has been released.
OA/ RA ACTUATOR;BELIMO 3 wire floating | X13611005040 | ACT00459
OA/ RA Acutator bolt (3) | X25240208010 |  |  | REPLACE X13611011020 (ACTUATOR; ROTARY W/ CON) IN THE
OA/ RA Acutator bracket (1) | X05011477010 |  |  | PART NUMBER X13611407010 (ACTUATOR; ROTARY W/ CON) WILL
OA/ RA Acutator nut (3) | X28060206090 |  |  | FOLLOWING PARENT PARTS:
Retainer rod for filters (this one in 1250 & 1500 units 1Ea) | X25380068010 | ROD01202
Retainer rod for filters (this one goes in all units 2ea) | X25380067010 | ROD01201
Snubber 1uF (black epoxy on end) | X1301032301
Snubber 2uF (yellow epoxy on end) | X1301032302
Speed nut | X28061600000
Stud | X25180043010
Subbase Filler panel 2" |  |  | 4619-1297-0100
Subbase Filler panel 4" |  |  | 4619-1297-0200 | 461833300100 (ASSY; HORZ. F&B-3P.MOD)
Subbase Filler panel 6" |  |  | 4619-1297-0300 | 461911450100 (COILB;FB 3-WIRE ACTUATOR)
VALVE;THERM EXP (R22) 1500 | X15111205040
VALVE;THERM EXP (R22) 750 / 1000 | X15111205020
VALVE;THERM EXP (R22) 1250 | X15111205030
VALVE;TXV.38DSx.63DS 2TN (R410A) 1250 / 1500 | X15111282030 | sporlan bbize 3 | 3 Ton
VALVE;TXV.38DSx.63DS 2TN (R410A) 750 / 1000 | X15111282020 | sporlan bbize 2 | 2 ton
Washer | X22050027000
white plastic ring for access panel screw | x22010313020 |  |  | PART NUMBER X13611409020 (ACTUATOR; DAMPER) WILL
3 speed switch w/ harness |  |  | 351822260100
Leveling Feet (Screw and foot only) for VUVE or Sub-base | X25480034010 | SCR01287
Time Clock, Grasslin | X13290091040 | TMR00119

## HUV
Description | X Code | CATS | 4619
ECM Motor harness 208/230/277v | 461925940100
ECM Motor harness 115v | 461925940200
TXV - R22 ONLY | X15111205 ----01 THRU 07
PART No | TITLE | UNIT | TYPE
X15111205020 | VALVE;THERM EXP | 750 / 1000 | R22
X15111205030 | VALVE;THERM EXP | 1250 | R22
X15111205040 | VALVE;THERM EXP | 1500 | R22
X15111282020 | VALVE;TXV.38DSx.63DS 2TN | 750 / 1000 | 410
X15111282020 | VALVE;TXV.38DSx.63DS 2TN | 1250 / 1500 | 410
x15111775030 | 3 ton Valve TXV, .38 inlet, .88 outlet | HUVC 200 | 410. Adjustable.
Snubber (1 uF) | X13010323010 | SPS00058
Snubber (2 uF) | X13010323020 | SPS00059
Autotransformer 1000VA, 120 Volt |  | X13550502060
Autotransformer 1300VA, 120 Volt |  | X13550502070
Autotransformer 375VA, 120 Volt |  | X13550502010

## LOCH-STAT Issue
Serial # | TIM # | Issue | Notes
T16L43233 | 3859125 | LOCH | Worked with Kevin - Verified Ecm was not changed. Shutting off
T16J39163 | 3860855 | LOCH | Set to torque mode - motor shutting down
T17J39818 | 3865458 | LOCH | Would not reach 983 RPM - LOCH and Low Airflow Diagnostic

## BCXD 2-24-15
Description | X-code/part # | Mnemonic | Notes
Blower coil
WIRE; HARNESS; PERSONALITY BCXD | 501998770100 | WIR07335
WIRE; HARNESS; PERSONALITY BCXD | 501998770200 | WIR07401
WIRE; HARNESS; PERSONALITY BCXD | 501998770300 | WIR07336
WIRE; HARNESS; PERSONALITY BCXD | 501998770400 | WIR07402
Motor harnesses 01 - 08 Up to 1 HP | 501998750100
Motor harnesses 01 and 02 1.5 - 3HP | 501999910100
Motor harnesses 01 and 02 1.5 - 3HP | 501999910200 | WIR07588

## High Rise 2021
Description | Trane number | WEBCATS
Ball valve - return | X15333073001

## Belimo 2018 Parts
Valve X-code | Belimo Part # | Service Part # | Description | Max CV
X15333076001 | Z2050QS-F | VAL18759 | VALVE; BODY, 2-WAY, .50 | 1.4
X15333076002 | Z2050QS-J | VAL18760 | VALVE; BODY, 2-WAY, .50 | 5.9
X15333077001 | Z2075QS-K | VAL18761 | VALVE; BODY, 2-WAY, .75 | 9.8 | Search Belimo site for exact model number. Small differences exist.
X15333078001 | Z3050QS-E | VAL18762 | VALVE; BODY, 3-WAY, .50 | 1
X15333078002 | Z3050QS-H | VAL18763 | VALVE; BODY, 3-WAY, .50 | 2.7
X15333079001 | Z3075QS-J | VAL18764 | VALVE; BODY, 3-WAY, .75 | 4.6
X15333082001 | B222 | VAL18765 | VALVE; BODY, 2-WAY, 1.0 | 7.4
X15333082002 | B223 | VAL18766 | VALVE; BODY, 2-WAY, 1.0 | 10
X15333080001 | B318 | VAL18767 | VALVE; BODY, 3-WAY, .75 | 7.4
X15333083001 | B322 | VAL18768 | VALVE; BODY, 3-WAY, 1.0 | 7.4
X15333083002 | B323 | VAL18769 | VALVE; BODY, 3-WAY, 1.0 | 10
X15333081001 | B225HT1160 | VAL18770 | VALVE; BODY, 2-WAY, 1.0 | 11.6
Actuator X- code | Belimo Part No | Service part# | Description |  |  |  | Stroke Time
X13612093001 | CQB24-3 | ACT00888 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 4 |  |  | 3 wire floating | 49
X13612093002 | CQB24-3 | ACT00889 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 5 |  |  | 3 wire floating | 55
X13612093003 | CQB24-3 | ACT00890 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 6 |  |  | 3 wire floating | 62
X13612093004 | CQB24-3 | ACT00891 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION N |  |  | 3 wire floating | 68
X13612093005 | CQB24-3 | ACT00892 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION No END STOP |  |  | 3 wire floating | 75
X13612094001 | CQB24-SR-R | ACT00893 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 4 |  |  | 2-10V | 49
X13612094002 | CQB24-SR-R | ACT00894 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 5 |  |  | 2-10V | 55
X13612094003 | CQB24-SR-R | ACT00895 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 6 |  |  | 2-10V | 62
X13612094004 | CQB24-SR-R | ACT00896 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION N |  |  | 2-10V | 68
X13612094005 | CQB24-SR-R | ACT00897 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION No END STOP |  |  | 2-10V | 75
X13612095001 | CQKB24-LL | ACT00898 | ACTUATOR; 2 WIRE, 2-WAY, CLIP POSITION 4 |  |  | 2 position NO | N/A
X13612095002 | CQKB24-LL | ACT00899 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 5 |  |  | 2 position NO | N/A
X13612095003 | CQKB24-LL | ACT00900 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 6 |  |  | 2 position NO | N/A
X13612095004 | CQKB24-LL | ACT00901 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION N |  |  | 2 position NO | N/A
X13612095005 | CQKB24-LL | ACT00902 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION No END STOP |  |  | 2 position NO | N/A
X13612096001 | CQKB24-RR | ACT00903 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 4 |  |  | 2 position NC | N/A
X13612096002 | CQKB24-RR | ACT00904 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 5 |  |  | 2 position NC | N/A
X13612096003 | CQKB24-RR | ACT00905 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION 6 |  |  | 2 position NC | N/A
X13612096004 | CQKB24-RR | ACT00906 | ACTUATOR; 3 WIRE, 2-WAY, CLIP POSITION N |  |  | 2 position NC | N/A
X13612096005 | CQKB24-RR | ACT00907 | ACTUATOR; 2 WIRE, 2-WAY, CLIP POSITION No END STOP |  |  | 2 position NC | N/A
X13612097001 | TR24-3 US | ACT00908 | ACTUATOR MOD |  |  | 3 wire floating | 90
X13612098001 | TR24-SR US NC | ACT00909 | ACTUATOR 2-10V |  |  | 2-10V | 90
X13612099001 | TFRB24 | ACT00910 | ACTUATOR NO/NC |  |  | 2 position Spring return | 75
X13612100001 | LRB24-3 | ACT00911 | ACTUATOR MOD |  |  | 3 Wire floating, non-spring return | 90
X13612101001 | LF24 US | ACT00912 | ACTUATOR NO/NC | Stronger actuator B322 is too large for TFRB actuator |  | 2 position Spring return | 75