## Slide 1: How to backup and re-configure a unit with UC800 controller
RTAE, RTHD and RTAF units.

## Slide 2: How to Backup
Open TU and connect to the unit with a USB “type A” to “type B” cable.
Select “Direct connection” and click “Connect”

## Slide 3: How to Backup
Go to “Utilities” and select “Backup Utility”

## Slide 4: How to Backup
Make sure the check mark is selected for the unit you are connected to and then click “Next”.

## Slide 5: How to Backup
Make sure the file (.zip) is being saved to the correct folder, then click “Next”

## Slide 6: How to Backup
Click “Start”

## Slide 7: How to Backup
Be patient as this process may take several minutes

## Slide 8: How to Backup
Once the file has been saved you will get a message indicating backup successful, click “Finish”
Backup process complete.

## Slide 9: How to Re-configure
Open TU and connect to the unit with a USB “type A” to “type B” cable.
Using TU connect to the UC800 and download the latest MP.
Go to “Utilities” and then select “File Transfer Utility”

## Slide 10: How to Re-configure
You will get a message indicating data log collection will be interrupted, click Yes to save the current log or No to discard it.

## Slide 11: How to Re-configure
Make sure the check mark is selected for the unit you are connected to, click “Next”
Do not check the TD7 box.

## Slide 12: How to Re-configure
Click “Browse” and select the .zip file previously backed up for the desired unit.

## Slide 13: How to Re-configure
Search and select the correct .zip file and click “Open”

## Slide 14: How to Re-configure
Once the correct file has been selected click “Next”

## Slide 15: How to Re-configure
On the next screen click “Start”

## Slide 16: How to Re-configure
Restoring configuration in progress, this may take a few minutes, do not disconnect or power down.

## Slide 17: How to Re-configure
Once the re-configuration is complete you will get a message indicating “Successful”, click “Finish”
Re-configuration process complete.

## Slide 18: How to Re-configure
To confirm, go to “Utilities” and then “Configuration” and confirm the correct the settings.