## Calcs
CGWF and RTWA Water Regulating Valve Sizing
For V46 and V43 Johnson Controls Water Regulating Valves
**This file needs to be used in conjunction with Johnson Controls V46 Product/Technical Bulletin, LIT #: LIT-125687
and V43 Product/Technical Bulletin, LIT #: LIT-125683
INPUTS | Maximum Condenser Flow | 200 | GPM | Based on operating conditions
| Condenser Pressure Drop | 4.21 | PSIG | Obtained from TOPPS output
| Condenseing Temp | 105 | Deg F | Generally 7-10 Deg F above condenser leaving water temp
| Condensing Pressure | 210.7 | PSIG | Refer to R22 Refrigerant Table Tab below to obtain pressure from cond. Temp
| Maximum Ambient Temp | 90 | Deg F | Based on expected max ambient for the space the valve is located in
| Pressure @ Max Ambient Temp | 168.4 | PSIG | Refer to R22 Refrigerant Table Tab below to obtain pressure from Ambient Temp
| Supply Water Pressure (per valve) | 35 | PSIG | Based on supply from cooling tower, pump, or city water
| Addition Installed Piping PD | 4 | PSIG | Additional pressure drop by any piping/fittings between condenser outlet and valve
OUTPUTS | Closing Pt Pressure | 168.4 | PSIG | Refer to step 2 below
| Opening Pt Pressure | 175.4 | PSIG | Refer to step 2 below
| Operating Head Pressure | 210.7 | PSIG | Refer to step 2 below
| Head Pressure Rise | 35.3 | PSIG | Refer to step 2 below
| Pressure Drop Across Valve | 26.79 | PSIG | Refer to step 3 below
Step 1. | Determine Maximum Condenser flow (gpm)
ex. 200 gpm
Step 2. | Determine Head Pressure Rise above Valve Opening Point (PSIG)
ex. Look at output above for value
Closing Pt is pressure @ max ambient (refer to 134a Refrigerant Table Tab for pressure)
Opening pt = closing pt pressure + 7 PSIG
Operating Head Pressure = Condensing Pressure
Head Pressure Rise = Operating Head Press - Opening Pt.
Step 3. | Minimum Pressure = Supply Water Pressure
ex. System pressure =70 psig so each valve sees 35 psig
Additional Pressure drops = Condenser Pressure Drop + Installed Piping
ex. Condenser PD @ 200 gpm is 4.2 psig + 4 psig for additional piping
Pressure Drop Across Valve = Minimum Pressure Drop + Additional Pressure Drop
Step 4. | Find Valve that meets Head Pressure Rise, Pressure Drop Across the Valve, and Flow Rate
Make sure the maximum flow the valve can handle is greater than the maximum system
| flow through each valve |  |  | ex. In this case we need two V46 2.5" valves
P1
| Pt=P1+P2 |  |  | Valve Ckt #1
from condenser
| Pt |  |  |  | Pt
Valve Ckt #2
P2

## R22 Refrigerant Table
Vapor Pressures
Temp | HFC-22
(deg F) | (PSIG)
10 | 32.8
15 | 37.7
20 | 43
25 | 48.8
30 | 54.9
35 | 61.4
40 | 68.5
45 | 76
50 | 84
55 | 92.6
60 | 101.6
65 | 111.2
70 | 121.4
75 | 132.2
80 | 143.6
85 | 155.7
90 | 168.4
95 | 181.8
100 | 195.9
105 | 210.7
110 | 226.4
115 | 242.7
120 | 259.9
125 | 277.9
130 | 296.8
135 | 316.6
140 | 337.2
145 | 358.9
150 | 381.5