## Current Products
Pressure relief Valve sizes/info.
| Pressure |  | # of |  |  | Factory Threads | Customer
Product | Region | Location | Valves | PSI | Lba/min | (Size) | threads | Manufacturer | Part # on Box | Part # on Valve | TRANE PN
RTAC Medium | Low | Evap Tube sheet | 2 | 200 | 17.3 | 7/8-14 UNF - 2A | 0.625" MFL | Mueller | BQ35413-200 psi | B-35413 | X15120712010
(140-250 tons) | High | Internal to Comp. | - | - | - | - | - | -
|  | Top of Oil Seperator | 2 | 350 | 6.3 | 1/4"-18 NPTE | 0.380" MFL | Mueller | AG15501 350psi | A-15501 | X15120262020
RTAC Large | Low | Evap Tube sheet | 3, 4 | 200 | 28.9 | 7/8-14-UNF-2B SAE J-1926 | 3/4" NPTFI | Mueller | B-34444-200 psi | B-34444 | X15120264010
(275-500 tons) | High | Internal to Comp. | - | - | - | - | - | -
|  | Top of Oil Seperator | 2 | 350 | 6.3 | 1/4"-18 NPTE | 0.380" MFL | Mueller |  | A-15501 | X15120262020
=================================================================================================================================================
RTHD w/o isolation | LowG evaps | Evap. Barrel | 1 | 200 | 78.8 | 1 5/8" SAE O-Ring | 1 1/4" NPTFemale | Mueller | BQ34580 | B-34580 | X15120265010
| Low | Evap. Barrel | 1 | 200 | 48 | 1 5/16" SAE O-Ring | 1" NPTFemale | Mueller | BQ34519 | B-34519 | X15120260010
| High | Cond. Barrel | 2 | 200 | 48 | 1 5/16" SAE O-Ring | 1" NPTFemale | Mueller | BQ34519 | B-34519 | X15120260010
RTHD w/ isolation | LowG evaps | Evap. Barrel | 1 | 200 | 78.8 | 1 5/8" SAE O-Ring | 1 1/4" NPTFemale | Mueller | BQ34580 | B-34580 | X15120265010
| Low | Evap. Barrel | 1 | 200 | 48 | 1 5/16" SAE O-Ring | 1" NPTFemale | Mueller | BQ34519 | B-34519 | X15120260010
| High | Oil Separator Candy Cane | 3 | 200 | 78.8 | 1 5/8" SAE O-Ring | 1 1/4" NPTFemale | Mueller | BQ34580 | B-34580 | X15120265010
| HighB Comp. | Oil Separator Candy Cane | 2 | 200 | 78.8 | 1 5/8" SAE O-Ring | 1 1/4" NPTFemale | Mueller | BQ34580 | B-34580 | X15120265010
| High | Cond. Barrel | 2 | 200 | 48 | 1 5/16" SAE O-Ring | 1" NPTFemale | Mueller | BQ34519 | B-34519 | X15120260010
=================================================================================================================================================
RTWD | High | Cond. Barrel | 2, 4 | 300 | 25.4 | 7/8-14 UNF - 2A | 5/8" MFL | Mueller | BE35413-300 | B-35413 | X15120712020
| Low | Evap. Barrel | 2, 4 | 200 | 28.9 | 7/8-14 UNF - 2A | 3/4" NPTFemale | Mueller | B-34444-200 psi | B-34444 | X15120264010
RTUD | High | Oil Separator | 2 | 350 | 6.3 | 1/4-18 NPTE | 0.380" MFL | Mueller |  | A-15501 | X15120262020
| Low | Evap. Barrel | 2 | 200 | 28.9 | 7/8-14 UNF - 2A | 3/4" NPTFemale | Mueller | B-34444-200 psi | B-34444 | X15120264010
=================================================================================================================================================
RTAE | Low | Evap Tube Sheet | 2 | 200 | 17.3 | 7/8-14 UNF - 2A | 5/8" MFL | Mueller | BQ35413-200 psi | B-35413 | X15120712010
| High | Top of Oil Separator | 2 | 350 | 6.3 | 1/4" NPT | 3/8" FL | Mueller | AG15501 350psi | A-15501 | X15120262020
=================================================================================================================================================
RTAF | Low | Evap Tube sheet | 2 | 200 | 17.3 | 7/8-14 UNF - 2A | 0.625" MFL | Mueller | BQ35413-200 psi | B-35413 | X15120712010
(115-250 tons) | High | Top of Oil Seperator | 2 | 350 | 6.3 | 1/4"-18 NPTE | 3/8" MFL | Mueller | AG15501 350psi | A-15501 | X15120262020
RTAF | Low | Evap Tube sheet | 2 | 200 | 28.9 | 7/8-14 UNF - 2A | 3/4" NPTFI | Mueller | B-34444-200 psi | B-34444 | X15120264010
(280-350 tons) | High Circuit #2 | Top of Oil Seperator | 1 | 350 | 6.3 | 1/4"-18 NPTE | 3/8" MFL | Mueller | AG15501 350psi | A-15501 | X15120262020
| High Circuit #1 |  | 1 | 350 | 13.3 | 3/4"-18 NPTE | 3/8" MFL | Mueller | AG15502 350psi | A-15502 | X15121303001
RTAF | Low | Evap Tube sheet | 2 | 200 | 28.9 | 7/8-14 UNF - 2A | 3/4" NPTFI | Mueller | B-34444-200 psi | B-34444 | X15120264010
(410-500 tons) | High | Top of Oil Seperator | 2 | 350 | 13.3 | 3/8"-18 NPTE | 3/8" MFL | Mueller | AG15502 350psi | A-15502 | X15121303001
=================================================================================================================================================
CGAM | Does not have refrigerant relief valves - see HVAC Knowledge Center wave51235
updated 3/28/16
Note on L5: Becky Trujillo: 1/19/09 - Change request is pending to change to X15120712010
Note on L41: Becky Trujillo: 1/19/09 - Change request is pending to change to X15120712010

## Obsolete Products
Pressure relief Valve sizes/info. -- 1/2010
| Pressure |  | # of |  |  | Factory Threads | Customer
Product | Region | Location | Valves | PSI | Lba/min | (Size) | threads | Manufacturer | Part # on Box | Part # on Valve | TRANE PN
CGWD/CCAD
| Low | Evap. Head | 1, 2 | 300 | 11.5 | 1/4" NPT | 3/8" SAE MFL | Mueller
| High | Cond. Barrel | 1, 2 | 450 | 37.6 | 1/2" NPT | 5/8" SAE MFL | Mueller
RTWA/RTUA
| Low | Evap. Head | 2 | 300 | 11.5 | 1/4" NPT | 3/8" SAE MFL | Mueller | BE33752
| High | Cond. Barrel | 2 | 450 | 37.6 | 1/2" NPT | 5/8" SAE MFL | Mueller | AJ15504
RTAA Ph I
(130-215) | Low | Evap. Head/circuit | 2 | 300 | 11.5 | 1/4" NPT | 3/8" SAE MFL | Mueller
| High | Discharge line/compressor | 2 | 450 | 37.6 | 1/2" NPT | 5/8" SAE MFL | Mueller
RTAA Ph II
(240-400) | Low | Evap. Head/circuit | 2 | 300 | 11.5 | 1/4" NPT | 3/8" SAE MFL | Mueller
| High | Discharge line/compressor | 3, 4 | 450 | 37.6 | 1/2" NPT | 5/8" SAE MFL | Mueller
RTAA Ph III
(70-125) | Low | Evap. Head/circuit | 2 | 300 | 11.5 | 1/4" NPT | 3/8" SAE MFL | Mueller
| High | Internal to Comp. | - | - | - | - | - | -
RTHB | Low | Evap. Barrel | 1 | 300 | 42.5 | 3/4" NPTFemale | 3/4" NPTFemale | Mueller
| High | Comp. Oil separator | 1 | 300 | 42.5 | 3/4" NPTFemale | 3/4" NPTFemale | Mueller
| High | Cond. Barrel | 2 | 300 | 42.5 | 3/4" NPTFemale | 3/4" NPTFemale | Mueller
Evp. 20-60 | Low | Hole for valve on evap. head | 1, 2 | 300 | 11.5 | 0.25 | 3/8" Flare | Mueller
Not supplied
| Pressure |  | # of |  |  | Factory Threads | Customer
| Region | Location | Valves | PSI | Lba/min | (Size) | threads | Manufacture
Product | High | AJ15504 |  | 450 | 37.6 | 1/2 NPT | 5/8" SAE MFL | Mueller
West Plant | Low | BE33752 |  | 300 | 11.5 | 1/4 NPT | 3/8" SAE MFL | Mueller
| Low | BQ34580 |  | 200 | 78.8 | 1 5/8" SAE O-Ring | 1 1/4" NPTFemale | Mueller
RTHD | High/Low | BQ34519 |  | 200 | 48 | 1 5/16" SAE O-Ring | 1" NPTFemale | Mueller
| High/Low | AE15506 |  | 300 | 42.5 | 3/4" NPTFemale | 3/4" NPTFemale | Mueller