RTAC Liquid Level Sensor Upgrade

There are 3 options of Liquid level sensors in the options setup menu. Make the appropriate selection based on the sensors installed on the unit.  The one with the “Level Sensor with Integrated Electronics” in the description needs to be selected if you have the 56MM sensor.

In some cases the liquid level sensors must be upgraded to be used in Adaptiview. First try binding the way they are. If they bind, no further action is required. If they will not bind, they will show up as extra LLIDs. Unbind these and rebind. During rebinding update the LLID firmware when prompted. Do these one at a time. May have to go through the unbind/rebind process a second time after upgrading. Follow the attached screenshots and instructions if necessary.

The UC800 RTAC firmware requires the level sensor to have llid firmware version 3 or greater

If not, the following error message will be displayed when attempting to bind the device

To correct this, the llid firmware must be upgraded.

Select upgrade llid…

When the confirmation dialog box appears, select the device with the magnet

Press OK, download will proceed

The following dialog box will appear if successful

Rebuild binding view

The level sensor will have a status of red X

Select the device and Unbind it

Reselect the device and bind it again

The status should now be bound