Product: All Terminal Products

Subject: Fire Alarm Shutdown- UC400 or CSTI Control Option

Details:

NOTE: Trane does not offer a point to shutdown the fan.

Recommendation is to break the 24v power to the control board.

With UC400 or Symbio break J15-5 from the transformer.

A diagram of a circuit

Description automatically generated

With CSTI break J12-1 from the transformer.

A diagram of numbers and lines

Description automatically generated