## Sheet1
https://tranetechnologies-my.sharepoint.com/personal/tony_cook_tranetechnologies_com/Documents/Desktop/Schematics and Tech Literature/Voyager 3/Symbio 700 docs/[1287 LED diagnostics.xlsx]Sheet1
2018-08-15 | Last edited | added missed LED code for ID plug failure
2024-03-19 11:56 | printed
Note: LED failures and modbus failures codes are same. While the control provides detial interface for states and warnings, LED display allows only partial view on warnings and states.
Comon for Modbus and LED display
| failures | display code (decimal) | color | description
| eFLAME_PRIME | 11 | RED | flame is detected out side of normal operations by prime burner flame rod
| eFLAME_SPLIT | 21 | RED | flame is detected out side of normal operations by split burner flame rod.
| eFLAME_PRIME_SPLIT | 31 | RED | flame is detected out side of normal operations by prime and split burner flame rods.
| eAIR_ZERO_LO | 41 | RED | air pressure low switch is closed when inducer is off
| eAIR_ZERO_HI | 42 | RED | air pressure high switch is closed when inducer is off or at low speed
| eAIR_FLOW_LO | 43 | RED | air pressure low switch is open when it is expected to be closed
| eAIR_FLOW_HI | 44 | RED | air pressure high switch is open or closed when it is expected to be closed or open
| eFUSE | 45 | RED | fuse is open
| ePRIMARY_LIMIT | 51 | RED | primary limit is open
| eNO_IGNITION_PRIME | 12 | RED | prime burner exceeds a number of trials for ignitions.
| eNO_IGNITION_SPLIT | 22 | RED | split burner exceeds a number of trials for ignitions. Prime burner will remain operational if this failure is detected
| eNO_IGNITION_PRIME_SPLIT | 32 | RED | reserved for future use
| eFLAME_DROP_OUT_PRIME | 13 | RED | prime burner flame loss count exceeds a threshold
| eFLAME_DROP_OUT_SPLIT | 23 | RED | split burner flame loss count exceeds a threshold. Prime burner remains operational.
| eFLAME_DROP_OUT_PRIME_SPLIT | 33 | RED | split burner flame loss count exceeds a threshold. Prime burner remains operational .
| eGAS_VALVE_PRIME | 14 | RED | prime burner gas valve is shorted to 24VAC
| eGAS_VALVE_SPLIT | 24 | RED | split burner gas valve is shorted to 24VAC
| eGAS_VALVE_PRIME_SPLIT | 34 | RED | prime and split burner gas valve is shorted to 24VAC
| eGAS_VALVE_HI_PRIME | 15 | RED | Prime burner modulation/staging failure. The failure indicates that gas valve state is low when it must be high, o high when it must be low
| eGAS_VALVE_HI_SPLIT | 25 | RED | Split burner modulation/staging failure. The failure indicates that gas valve state is low when it must be high, or high when it must be low
| eGAS_VALVE_HI_PRIME_SPLIT | 35 | RED | Prime and split burner modulation/staging failure. The failure indicates that gas valve state is low when it must be high, or high when it must be low
| eID_PLUG | 54 | RED | ID plug failure. Reserved for future use.
| eSYSTEM | 55 | RED | control board failure, gas valve relays, safety relays, etc
Specifc for LED display
| warnings | display code (decimal) | color | description
| prime burner flame rod aged waring | 11 | YELLOW | indicates that flame rod indicartes low current.
| split burner flame rod aged waring | 21 | YELLOW | indicates that flame rod indicates low current.
| prime and split burner flame rod aged waring | 31 | YELLOW | indicates that both flame rods measured low current.
| prime burner retry on the ignition or flame dropout | 13 | YELLOW | call for heat prime burner is in RETRY
| split burner retry on the ignition or flame dropout | 23 | YELLOW | call for heat split burner is in RETRY
| lost communication | 52 | YELLOW | control is in idle mode, keep alive timeout is expired
| manual override | 53 | YELLOW | control is in idle mode, manual override is in off position
Speciifc for LED display
| normal operations | display code (decimal) | color | description
| control is idle, prime and split functional | 11 | GREEN | Prime burner and split burner is in state OFF.
| call for heat, statup | 12 | GREEN | Burner state PURGE
| call for heat, prime heating heating | 13 | GREEN | Prime burner is runnig, burner states GAS_ON, WARMUP, RUN
| call for heat, prime and/or split heating | 33 | GREEN | Split and prime burners are running.
Speciifc for LED display
| split burner in lockout, prime is active operations | display code (decimal) | color | description
| control is idle, split burner is in lockout | 11 | GREEN/YELLOW | Prime burner is in off. Split burner is in lockout.
| call for heat, startup, split is in lockout | 12 | GREEN/YELLOW | Burner state PURGE. Split burner is in lockout.
| ca;; for heat, prime heating, split is in lockout | 13 | GREEN/YELLOW | rime burner is runnig. Burner states GAS_ON, WARMUP, RUN. Split burner is in lockout.
Speciifc for LED display
| special failures | display code | color | description
| 24VAC failure, ID Plug, or MCU initialization RA state, hard lockout | steady | RED | control is not functional.
| ID Plug failure | rapid | RED | id plug failure to initialize, control is not functional