## 0.5-5 ton WSE Piping
0.5-5 Ton WSE Piping diagram
Waterside Economizer Coil
Please disregard the arrow direction on the valve body.
Heat Pump Operation ( Default)
Port AB opens to Port A
Water flows thru the Tee to the unit heat exchanger thru Unit corrner water in fitting |  |  |  |  | Note: Low entering air protection not provided
WSE operation ( 24V applied to the actuator open ( Black and White actuator leads)
Port AB opens to port B |  |  |  |  | TEE
Water flows thru WSE coil and then to the unit water in fitting to unit heat exchanger. |  | Flexible Hose connected to this outlet gets routed to the unit water inlet on the corner of the unit
Port A
To unit water Inlet connection
Port B
WSE Two position Three Way Valve
Port AB
( Loop water supply inlet )