## RTA-WA-CG
ASME UNIT SPECIFICATIONS |  |  |  |  | RTAA/UA/WA CG/CC Evap Material: |  |  | A-139 |  | RTWA Cond Material: |  | A53-B ERW |  | Evap Tube Material: B-359
RTAA/UA/WA CG/CC |  |  |  |  | CG Cond Material: |  |  | A-513 or A-53 |  | All Tube Sheet Material: |  | A516 Grade 70 |  | RTWA Cond Tube Material: B-359 or B-543
| No. Evap Tubes | Nom Evap Tube Diameter (in) | Nom Evap Tube Wall Thickness (in) | No. Cond Tubes | Nom Cond Tube Diameter (in) | Nom Cond Tube Wall Thickness (in) | Evap MAWP (psi) | Cond MAWP (psi) | Evap ASME Test Pressure (psi) | Cond ASME Test Pressure (psi) | Shell Side Test Press (psi) | Evap Waterbox Hydro Test Press (psi) | Evap Relief Valve Set (psi) | Cond Relief Valve Set (psi) | Evap Supply Gasket Tab Position | Evap Return Gasket Tab Position | Evap Tube Roll Torque (in-lb) | Cond Tube Roll Torque (in-lb) | Evap Waterbox Bolt Torque (ft-lb) | Evap Vacuum Test (microns)
RTAA 70 | 158 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | UP | 55-58 | NA | 85 | 275
RTAA 80 | 178 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | UP | 55-58 | NA | 85 | 275
RTAA 90 | 207 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | UP | 55-58 | NA | 85 | 275
RTAA 100 | 236 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | UP | 55-58 | NA | 85 | 275
RTAA 110 | 196 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 85 | 275
RTAA 125 | 248 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 85 | 275
RTAA 130 | 231 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 85 | 275
RTAA 140 | 248 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 85 | 275
RTAA 155 | 273 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 85 | 275
RTAA 170 | 298 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 85 | 275
RTAA 185 | 327 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 85 | 275
RTAA 200 | 356 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 85 | 275
RTAA 215 | 710 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 165 | 275
RTAA 240 | 424 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 165 | 275
RTAA 270 | 475 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 165 | 275
RTAA 300 | 530 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 165 | 275
RTAA 340 | 600 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 165 | 275
RTAA 370 | 655 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 165 | 275
RTAA 400 | 710 | 0.625 | 0.023 | NA | NA | NA | 300 | NA | 375 | NA | 322 | 600 | 300 | NA | UP | DOWN | 55-58 | NA | 165 | 275
CG/CC 20 | 64 | 0.625 | 0.023 | 21 | 0.75 | 0.026 | 300 | NA | 375 | NA | 563 | 600 | 300 | 450 | UP | DOWN | 35-40 | 40-45 | 65 (87 max) | 275
CG/CC 25 | 76 | 0.625 | 0.023 | 26 | 0.75 | 0.026 | 300 | NA | 375 | NA | 563 | 600 | 300 | 450 | UP | DOWN | 35-40 | 40-45 | 65 (87 max) | 275
CG/CC 30 | 96 | 0.625 | 0.023 | 32 | 0.75 | 0.026 | 300 | NA | 375 | NA | 563 | 600 | 300 | 450 | UP | DOWN | 35-40 | 40-45 | 65 (87 max) | 275
CG/CC 40 | 126 (84 W/C) | 0.625 | 0.023 | 42 | 0.75 | 0.026 | 300 | NA | 375 | NA | 563 | 600 | 300 | 450 | UP | DOWN | 35-40 | 40-45 | 65 (87 max) | 275
CG/CC 50 | 104 | 0.625 | 0.023 | 52 | 0.75 | 0.026 | 300 | NA | 375 | NA | 563 | 600 | 300 | 450 | UP | DOWN | 35-40 | 40-45 | 65 (87 max) | 275
CG/CC 60 | 126 (178 HE) | 0.625 | 0.023 | 74 | 0.75 | 0.026 | 300 | NA | 375 | NA | 563 | 600 | 300 | 450 | UP | DOWN | 35-40 | 40-45 | 65 (87 max) | 275
RTW/RTU 70 | 158 | 0.625 | 0.023 | 62 (74 long) | 0.75 | 0.026 | 300 | 450 (RTW) | 375 | 563 | NA | 600 | 300 | 450 | UP | UP | 55-58 | 45-50 | 85 | 275
RTW/RTU 80 | 178 | 0.625 | 0.023 | 74 (86 long) | 0.75 | 0.026 | 300 | 450 (RTW) | 375 | 563 | NA | 600 | 300 | 450 | UP | UP | 55-58 | 45-50 | 85 | 275
RTW/RTU 90 | 207 | 0.625 | 0.023 | 87 (103 long) | 0.75 | 0.026 | 300 | 450 (RTW) | 375 | 563 | NA | 600 | 300 | 450 | UP | UP | 55-58 | 45-50 | 85 | 275
RTW/RTU 100 | 236 | 0.625 | 0.023 | 100 (120 long) | 0.75 | 0.026 | 300 | 450 (RTW) | 375 | 563 | NA | 600 | 300 | 450 | UP | UP | 55-58 | 45-50 | 85 | 275
RTW/RTU 110 | 207 | 0.625 | 0.023 | 110 (130 long) | 0.75 | 0.026 | 300 | 450 (RTW) | 375 | 563 | NA | 600 | 300 | 450 | UP | DOWN | 55-58 | 45-50 | 85 | 275
RTW/RTU 125 | 236 | 0.625 | 0.023 | 120 (140 long) | 0.75 | 0.026 | 300 | 450 (RTW) | 375 | 563 | NA | 600 | 300 | 450 | UP | DOWN | 55-58 | 45-50 | 85 | 275
NAMEPLATE LOCATIONS: | [7 empty] | GENERAL NOTES:
20-60 / 70-125 / 130-200 |  | 12:00 position on tube sheet (refrigerant inlet side) | [5 empty] | Oil separators pneumatically tested to 565 psi
215 / 240-400 |  | 12:00 position on tube sheet (refrigerant outlet side) | [5 empty] | Aircooled condenser coils pneumatically tested to 500 psi
RTWA condensers |  | 12:00 position on shell 4-5 inches from tube sheet (relief valve side of shell)

## RTAC
ASME UNIT SPECIFICATIONS |  |  |  |  | Evap Material: A516 Grade 70 |  |  | Tube Sheet Material: A516 Grade 70
RTAC |  |  |  |  | LVS Material: A53-B ERW |  |  | Copper Tube Material: B-359
Unit Tonnage | No. Evap Tubes | Nom Evap Tube Diameter (in) | Nom Evap Tube Wall Thickness (in) | Evap MAWP (psi) | Oil Sep MAWP (psi) | Evap ASME Test Pressure (psi) | 150/300 Waterbox Hydro Test (psi) | Evap Relief Valve Set (psi) | Evap Tube Roll Torque (in-lb) | Evap Waterbox Bolt Torque (ft-lb) | Disch Line to Comp Bolt Torque (ft-lb) | Suct Line to Comp Bolt Torque (ft-lb) | Oil Sep Relief Valve Set (psi)
140 Standard (50/60 Hz) | 116 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
140 Premium (50/60 Hz) | 140 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
155 Standard (50/60 Hz) | 128 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
155 Premium (50/60 Hz) | 109 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
170 Standard (50/60 Hz) | 140 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
170 Premium (50/60 Hz) | 116 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
185 Standard (50/60 Hz) | 109 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
185 Premium (50/60 Hz) | 128 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
200 Standard (50/60 Hz) | 116 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
200 Premium (50/60 Hz) | 140 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
225 Standard (60 Hz) | 128 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
225 Premium (60 Hz) | 140 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
250 Standard (50 Hz) | 125 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
250 Standard (60 Hz) | 140 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
250 Premium (50 Hz) | 165 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
250 Premium (60 Hz) | 140 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
275 Standard (50/60 Hz) | 145 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
275 Premium (50/60 Hz) | 181 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
300 Standard (50/60 Hz) | 165 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
300 Premium (50/60 Hz) | 181 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
350 Standard (50 Hz) | 138 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
350 Standard (60 Hz) | 181 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
350 Premium (50/60 Hz) | 165 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
400 Standard (50/60 Hz) | 165 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
400 Premium (50/60 Hz) | 197 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
450 Standard (60 Hz) | 181 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
450 Premium (60 Hz) | 197 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
500 Standard (60 Hz) | 197 | 1 | 0.025 | 200 | 350 | 250 | 225 / 450 | 200 | 85 | 65 | 175 | 130 | 350
NAMEPLATE LOCATION:
On evaporator shell above liquid level sensor approximately 10 inches from tube sheet along longitudinal weld seam.

## RTH
ASME UNIT SPECIFICATIONS |  |  |  |  | Evap/Cond Material: A516 Grade 70
RTHB/RTHC |  |  |  |  | Tube Sheet Material: A516 Grade 70
Copper Tube Material: B-359 or B-543
| No. Tubes | Nom. Tube Diameter (in) | Nom. Tube Wall Thickness (in) | MAWP (psi) | Unit Proof Test (psi) | ASME Test Pressure (psi) | 150/300 PSI Waterbox Hydro Test (psi) | Relief Valve Set (psi) | Tube Roll Torque (in-lb) | Waterbox Bolt Torque (ft-lb)
RTHB EVAPS
130 | 68 | 0.028 | 1 | 300 | 375 | 375 | 225 / 450 | 300 | 65 | 35
150 | 78 | 0.028 | 1 | 300 | 375 | 375 | 225 / 450 | 300 | 65 | 35
180 | 98 | 0.028 | 1 | 300 | 375 | 375 | 225 / 450 | 300 | 65 | 35
215 | 112 | 0.028 | 1 | 300 | 375 | 375 | 225 / 450 | 300 | 65 | 35
255 | 139 | 0.028 | 1 | 300 | 375 | 375 | 225 / 450 | 300 | 65 | 35
300 | 157 | 0.028 | 1 | 300 | 375 | 375 | 225 / 450 | 300 | 65 | 35
380 | 196 | 0.028 | 1 | 300 | 375 | 375 | 225 / 450 | 300 | 65 | 35
450 | 224 | 0.028 | 1 | 300 | 375 | 375 | 225 / 450 | 300 | 65 | 35
RTHB COND
130 | 125 | 0.026 | 0.75 | 300 | 375 | 375 | 225 / 450 | 300 | 30 (25 for Cu/Ni) | 35
150 | 146 | 0.026 | 0.75 | 300 | 375 | 375 | 225 / 450 | 300 | 30 (25 for Cu/Ni) | 35
180 | 178 | 0.026 | 0.75 | 300 | 375 | 375 | 225 / 450 | 300 | 30 (25 for Cu/Ni) | 35
215 | 208 | 0.026 | 0.75 | 300 | 375 | 375 | 225 / 450 | 300 | 30 (25 for Cu/Ni) | 35
255 | 250 | 0.026 | 0.75 | 300 | 375 | 375 | 225 / 450 | 300 | 30 (25 for Cu/Ni) | 35
300 | 292 | 0.026 | 0.75 | 300 | 375 | 375 | 225 / 450 | 300 | 30 (25 for Cu/Ni) | 35
380 | 357 | 0.026 | 0.75 | 300 | 375 | 375 | 225 / 450 | 300 | 30 (25 for Cu/Ni) | 35
450 | 415 | 0.026 | 0.75 | 300 | 375 | 375 | 225 / 450 | 300 | 30 (25 for Cu/Ni) | 35
RTHC EVAPS
B1 Efficient | 100 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
B2 Efficient | 116 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
B3 Efficient | 140 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
D1 Efficient | 165 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
D2 Efficient | 181 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
C1 High Efficiency | 128 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
C2 High Efficiency | 140 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
B3 High Efficiency | 140 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
D3 High Efficiency | 197 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
F1 High Efficiency | 227 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
F2 High Efficiency | 243 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
E1 Premium Efficiency | 181 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
G1 Premium Efficiency | 304 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
G2 Premium Efficiency | 330 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
G3 Premium Efficiency | 376 | 1 | 0.025 | 200 | 250 | 250 | 225 / 450 | 200 | 85 | 65
RTHC COND
B1 Efficient | 150 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
B2 Efficient | 166 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
C1 Efficient | 150 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
C2 Efficient | 183 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
E1 Efficient | 214 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
E2 Efficient | 237 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
D1 High Efficiency | 150 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
D2 High Efficiency | 166 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
C2 High Efficiency | 183 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
E3 High Efficiency | 252 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
F2 High Efficiency | 270 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
F3 High Efficiency | 298 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
F1 Premium Efficiency | 222 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
G1 Premium Efficiency | 358 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
G2 Premium Efficiency | 429 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
G3 Premium Efficiency | 476 | 0.75 | 0.028 | 200 | 250 | 250 | 225 / 450 | 200 | 65 (45 for Cu/Ni) | 65
NAMEPLATE LOCATION
On evaporator shell above liquid level sensor approximately 8 inches from tube sheet along longitudinal weld seam.
On outward facing side of condenser shell (return end) approximately 8 inches from tube sheet along longitudinal axis.