## Single Relief Device
For a single relief device: |  | required entries are highlighted
Trane believes the facts and suggestions presented here to be accurate. However, final design and application decisions are your responsibility. Trane disclaims any responsibility for actions taken on the material presented.
Relief device description |  | Explanation (see Trane application manual APP-APM001-EN, dated Sep 2012)
Set pressure, P (psig) | 15 | Relief device is designed to open at this pressure
Absolute pressure at discharge, P2 (psia) | 14.7 | Absolute (atmospheric) pressure at outlet of discharge piping (sea level = 14.7 psia)
Discharge capacity, Cr (lb/min) | 64 | Refrigerant discharge capacity, as stamped on device or calculated by manufacturer
Relief device outlet diameter (in.) | 3 | Inside diameter of relief device outlet
Allowed back pressure at device outlet, P0 (psia) | 22.2 | As specified by manufacturer, or selected from following calculations:
| 16.95 | for a conventional relief valve (0.15 x P + atmospheric pressure), including RuptureGuard
| 18.45 | for a balanced relief valve (0.25 x P + atmospheric pressure)
| 22.2 | for a rupture disk alone, fusible plug, or pilot-operated valve (0.50 x P + atmospheric pressure)
Discharge pipe
Nominal pipe size (NPS) | 3 | Pick NPS from dropdown list (must be >= Relief device outlet diameter, Row 7) | Table E-1, ASHRAE 15-2010
Inside diameter of pipe, d (in.) | 3.068 | Value d from table at right for selected NPS (fills in automatically) | NPS, in. | ID (d), in. | f
Moody friction factor for pipe, f | 0.0173 | Value f from table at right for selected NPS (fills in automatically) | 0.5 | 0.622 | 0.0259
|  |  | 0.75 | 0.824 | 0.024
Allowable equivalent length of pipe, L (ft.) | 215.6334 | Maximum allowable equivalent length of discharge pipe for the entered NPS | 1 | 1.049 | 0.0225
(per Appendix E, ASHRAE Standard 15-2010) |  |  | 1.25 | 1.38 | 0.0209
|  |  | 1.5 | 1.61 | 0.0202
|  |  | 2 | 2.067 | 0.019
|  |  | 2.5 | 2.469 | 0.0182
|  |  | 3 | 3.068 | 0.0173
|  |  | 4 | 4.026 | 0.0163
|  |  | 5 | 5.047 | 0.0155
|  |  | 6 | 6.065 | 0.0149
|  |  | 8 | 7.981 | 0.0141
|  |  | 10 | 10.02 | 0.0135
|  |  | 12 | 11.938 | 0.0131
|  |  | 14 | 13.124 | 0.0133
Note on C8: per Appendix E, ASHRAE Standard 15-2010
Note on G15: Moody friction factor (fully turbulent flow)
Note on G27: Data for 0.5- through 6-inch pipe is from Appendix E in ASHRAE Standard 15-2010. Data for 8- through 14-inch pipe is from Crane Technical Paper No. 410.

## Headered identical reliefs
For identical relief devices |  | required entries are highlighted
connected to a common header: |  | * Note: All relief devices must have the same Cr, P, and relief device diameter.
Trane believes the facts and suggestions presented here to be accurate. However, final design and application decisions are your responsibility. Trane disclaims any responsibility for actions taken on the material presented.
Relief device description* |  | Explanation (see Trane application manual APP-APM001-EN, dated Sep 2012)
Set pressure, P (psig) | 15 | Relief device is designed to open at this pressure
Absolute pressure at discharge, P2 (psia) | 14.7 | Absolute (atmospheric) pressure at outlet of discharge piping (sea level = 14.7 psia)
Discharge capacity, Cr (lb/min) | 64 | Refrigerant discharge capacity, as stamped on device or calculated by manufacturer
Relief device outlet diameter (in.) | 3 | Inside diameter of relief device outlet
Allowed back pressure at device outlet, P0 (psia) | 22.2 | As specified by manufacturer, or selected from following calculations:
| 16.95 | for a conventional relief valve (0.15 x P + atmospheric pressure), including RuptureGuard
| 18.45 | for a balanced relief valve (0.25 x P + atmospheric pressure)
| 22.2 | for a rupture disk alone, fusible plug, or pilot-operated valve (0.50 x P + atmospheric pressure)
Feeder pipe from relief device outlet to header
Nominal pipe size (NPS) of feeder pipe | 3 | Pick NPS from dropdown list (must be >= relief device outlet diameter, Row 8) | Table E-1, ASHRAE 15-2010
Inside diameter of feeder pipe, d (in.) | 3.068 | Value d from table at right for selected NPS (fills in automatically) | NPS, in. | ID (d), in. | f
Moody friction factor for pipe, f | 0.0173 | Value f from table at right for selected NPS (fills in automatically) | 0.5 | 0.622 | 0.0259
"Resource" available | 3249.3698 | "Resource" available to be used in both feeder and common header pipes | 0.75 | 0.824 | 0.024
Length of feeder pipe, L (ft.) | 11 | Enter equivalent length of feeder pipe from relief device outlet to common header | 1 | 1.049 | 0.0225
"Resource" required | 165.7585 | "Resource" required in the feeder pipe (Row 20) must be < "Resource" available (Row 18) | 1.25 | 1.38 | 0.0209
Diameter of feeder pipe is: | OK |  | 1.5 | 1.61 | 0.0202
|  |  | 2 | 2.067 | 0.019
"Resource" remaining | 3083.6112 | "Resource" available to be used in common header pipe | 2.5 | 2.469 | 0.0182
|  |  | 3 | 3.068 | 0.0173
Common header pipe from feeders to outside |  |  | 4 | 4.026 | 0.0163
# of equal relief devices feeding common header | 3 | Relief devices must be same type, with same Cr, P, and device outlet diameter | 5 | 5.047 | 0.0155
Length of header pipe, L (ft.) | 40 | Enter equivalent length of header pipe leading to discharge outside | 6 | 6.065 | 0.0149
Nominal pipe size (NPS) of header pipe | 6 | Pick NPS from dropdown list | 8 | 7.981 | 0.0141
Inside diameter of header pipe, d (in.) | 6.065 | Value d from table at right for selected NPS (fills in automatically) | 10 | 10.02 | 0.0135
"Resource" required | 179.6836 | "Resource" required in the header pipe | 12 | 11.938 | 0.0131
Diameter OK based on area? | Yes | Cross-sectional area of header pipe (Row 41) must be >= sum of relief device cross-sectional areas (Row 40) | 14 | 13.124 | 0.0133
Diameter OK based on "resource"? | Yes | "Resource" required in the header pipe (Row 30) must be < "Resource" remaining (Row 23)
Diameter of header pipe is: | OK
Pipe cross-sectional area calculations
| 7.0686 | cross-sectional area of relief device
| 21.2058 | sum of relief device cross-sectional areas
| 28.8903 | cross-sectional area of the header pipe
Note on C9: per Appendix E, ASHRAE Standard 15-2010
Note on H16: Moody friction factor (fully turbulent flow)
Note on B18: Right-hand side of Equation 20 from the ASHRAE Standard 15-2001 User's Manual (pg 70)…see example H4
Note on B20: Left-hand side of Equation 20 from the ASHRAE Standard 15-2001 User's Manual (pg 70)…see example H4
Note on H28: Data for 0.5- through 6-inch pipe is from Appendix E in ASHRAE Standard 15-2010. Data for 8- through 14-inch pipe is from Crane Technical Paper No. 410.
Note on B30: Left-hand side of Equation 20 from the ASHRAE Standard 15-2001 User's Manual (pg 70)…see example H4

## Headered different reliefs
For different relief devices |  | required entries are highlighted
connected to a common header |  | * Note: Entries on rows 5, 7, and 15 must be left blank for unused device columns.
Trane believes the facts and suggestions presented here to be accurate. However, final design and application decisions are your responsibility. Trane disclaims any responsibility for actions taken on the material presented.
Relief device description* | Device 1 | Device 2 | Device 3 | Device 4 | Device 5 | Device 6 | Explanation (see Trane application manual APP-APM001-EN, dated Sep 2012)
Set pressure, P (psig) | 200 | 200 | 200 |  |  |  | Relief device is designed to open at this pressure
Absolute pressure at discharge, P2 (psia) | 14.7 | 14.7 | 14.7 |  |  |  | Absolute (atmospheric) pressure at outlet of discharge piping (sea level = 14.7 psia)
Discharge capacity, Cr (lb/min) | 78 | 48 | 48 |  |  |  | Refrigerant discharge capacity, as stamped on device or calculated by manufacturer
Relief device outlet diameter (in.) | 1.25 | 1.25 | 1.25 |  |  |  | Inside diameter of relief device outlet
Allowed back pressure at device outlet, P0 (psia) | 44.7 | 44.7 | 44.7 |  |  |  | As specified by manufacturer, or selected from following calculations:
| 44.7 | 44.7 | 44.7 | 0 | 0 | 0 | for a conventional relief valve (0.15 x P + atmospheric pressure), including RuptureGuard
| 64.7 | 64.7 | 64.7 | 0 | 0 | 0 | for a balanced relief valve (0.25 x P + atmospheric pressure)
| 114.7 | 114.7 | 114.7 | 0 | 0 | 0 | for a rupture disk alone, fusible plug, or pilot-operated valve (0.50 x P + atmospheric pressure)
Feeder pipe from relief device outlet to header | Feeder 1 | Feeder 2 | Feeder 3 | Feeder 4 | Feeder 5 | Feeder 6
Nominal pipe size (NPS) of feeder pipe | 1.5 | 1.25 | 1.25 |  |  |  | Pick NPS from dropdown list (must be >= relief device outlet diameter, Row 8) | Table E-1, ASHRAE 15-2010
Inside diameter of feeder pipe, d (in.) | 1.61 | 1.38 | 1.38 | 0 | 0 | 0 | Value d from table at right for selected NPS (fills in automatically) | NPS, in. | ID (d), in. | f
Moody friction factor for pipe, f | 0.0202 | 0.0209 | 0.0209 | #N/A | #N/A | #N/A | Value f from table at right for selected NPS (fills in automatically) | 0.5 | 0.622 | 0.0259
"Resource" available | 10622.768 | 12663.3991 | 12663.3991 | 1 | 1 | 1 | "Resource" available to be used in both feeder and common header pipes | 0.75 | 0.824 | 0.024
Length of feeder pipe, L (ft.) | 10 | 10 | 10 |  |  |  | Enter equivalent length of feeder pipe from the relief device outlet to common header | 1 | 1.049 | 0.0225
"Resource" required | 5624.1879 | 4603.4883 | 4603.4883 | 0 | 0 | 0 | "Resource" required in the feeder pipe | 1.25 | 1.38 | 0.0209
Diameter of feeder pipe is: | OK | OK | OK | OK | OK | OK | "Resource" required in the feeder pipe (Row 20) must be < "Resource" available (Row 18) | 1.5 | 1.61 | 0.0202
[8 empty] | 2 | 2.067 | 0.019
"Resource" remaining | 4998.5801 | 8059.9108 | 8059.9108 | 4998.5801 | 4998.5801 | 4998.5801 | "Resource" remaining to be used in common header pipe | 2.5 | 2.469 | 0.0182
Critical "resource" remaining | 4998.5801 | [5 empty] | Lowest "resource" remaining from individual feeder pipes calculations | 3 | 3.068 | 0.0173
[8 empty] | 4 | 4.026 | 0.0163
Common header pipe from feeders to outside | [7 empty] | 5 | 5.047 | 0.0155
Length of header pipe, L (ft.) | 30 | Enter equivalent length of header pipe leading to discharge outside | [5 empty] | 6 | 6.065 | 0.0149
Nominal pipe size (NPS) of header pipe | 3 | Pick NPS from dropdown list | [5 empty] | 8 | 7.981 | 0.0141
Inside diameter of header pipe, d (in.) | 3.068 | Value d from table at right for selected NPS (fills in automatically) | [5 empty] | 10 | 10.02 | 0.0135
Sum of Cr for all relief devices (lb/min) | 174 | [6 empty] | 12 | 11.938 | 0.0131
"Resource" required | 3341.5116 | "Resource" required in the header pipe | [5 empty] | 14 | 13.124 | 0.0133
Diameter OK based on area? | Yes | Cross-sectional area of header pipe (Row 42) must be >= sum of relief device cross-sectional areas (Row 41)
Diameter OK based on "resource"? | Yes | "Resource" required in the header pipe (Row 31) must be < Critical "resource" remaining (Row 24)
Diameter of header pipe is: | OK
Pipe cross-sectional area calculations
cross-sectional area of relief device | 1.2272 | 1.2272 | 1.2272 | 0 | 0 | 0
sum of relief device cross-sectional areas | 3.6816
cross-sectional area of the header pipe | 7.3927
Note on H9: per Appendix E, ASHRAE Standard 15-2010
Note on K16: Moody friction factor (fully turbulent flow)
Note on A18: Right-hand side of Equation 20 from the ASHRAE Standard 15-2001 User's Manual (p. 70)…see example H5
Note on A20: Left-hand side of Equation 20 from the ASHRAE Standard 15-2001 User's Manual (p. 70)…see example H5
Note on K28: Data for 0.5- through 6-inch pipe is from Appendix D in ASHRAE Standard 15-2019. Data for 8- through 14-inch pipe is from Crane Technical Paper No. 410.
Note on A31: Left-hand side of Equation 20 from the ASHRAE Standard 15-2001 User's Manual (p. 70)…see example H5