## Slide 1
Odyssey Wiring Summary
for Symbio 700 Pairing Scenarios

## Slide 2
Symbio/Odyssey Pairings
Trane Symbio 700, Trane Legacy, and non-Trane Scenarios
Notes: Since the combinations of condensers and air handlers is vast, each pairing is identified with a specific designation. Depending on the pairing designation, the wiring between the condenser, air handler, and thermostat / zone sensor varies. In addition, the number of wires required between the condenser and air handler varies with each pairing. Refer to the following diagrams for a high-level wiring summary. Refer to SS-SVN016* for additional wiring instructions.

## Slide 3
Air Handling Unit:
Condenser:
Pairing C or 3
Odyssey AHU with Electromechanical Condenser
Trane Odyssey
Two-Speed Fan
Electromechanical
2
Thermostat wire – 7 conductors. REQUIRED for this pairing scenario.
1
Thermostat wire – 5 conductors. REQUIRED for this pairing scenario.
1
Thermostat
2
Terminal
Strip
LTB1
B1
B2
Y1
Y2
R
EDC
Thermostat Wiring
Control Wiring
TR150
VFD
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
Notes: For pairings C and 3, the heating and cooling control is provided by the thermostat. Wire the thermostat to the relay board in the Trane Odyssey air handling unit. Use separate control wiring between the electromechanical condenser and Trane Odyssey air handler. Depending on the exact features of the air handler and condenser pairing, the number of conductors needed for that control wire may vary. Refer to the wiring diagrams in the installation guide SS-SVN016* for additional field wiring information.

## Slide 4
Air Handling Unit:
Condenser:
Pairing D
Odyssey Single Zone VAV (SZVAV) AHU with Electromechanical Condenser
Trane Odyssey
SZVAV
Electromechanical
2
Thermostat wire – 7 conductors. REQUIRED for this pairing scenario.
1
Thermostat wire – 5 conductors. REQUIRED for this pairing scenario.
1
2
Terminal
Strip
LTB1
B1
B2
Y1
Y2
R
EDC
Thermostat
Thermostat Wiring
Control Wiring
TR150
VFD
27
12
18
50
53
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
Notes: For pairings D, the heating and cooling control is provided by the thermostat. Wire the thermostat to the relay board that has been factory installed in the new Trane Odyssey air handler. Use separate control wiring to connect the air handler to the terminal strip in the electromechanical condenser. Depending on the exact features of the air handler and condenser pairing, the number of conductors needed for that control wire may vary. The VFD in the air handler is factory wired to the relay board and requires no field connection. Refer to the wiring diagrams in the installation guide SS-SVN016* for additional field wiring information.

## Slide 5
Air Handling Unit:
Condenser:
Pairing 4 (Thermostat)
Odyssey Constant Volume AHU with ReliaTel Condenser
Trane Odyssey
Constant Speed Fan
Trane ReliaTel
1
2
Thermostat wire – 7 conductors. REQUIRED for this pairing scenario.
1
Thermostat wire – 6 conductors. REQUIRED for this pairing scenario.
Thermostat
2
RTRM
Y2
COM
T
X2
W2
G
W1/O
Y1
R
ReliaTel
Terminal
Strip
LTB1
B1
R
CD
H1
H2
EF
Thermostat Wiring
Control Wiring
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
Notes: For pairing 4, the heating and cooling control is provided by the thermostat. Wire the thermostat to the RTRM controller in the Trane ReliaTel condenser. Use separate control wiring between the condenser and Trane Odyssey air handler. Depending on the exact features of the air handler and condenser pairing, the number of conductors needed for that control wire may vary. Refer to the wiring diagrams in the installation guide SS-SVN016* for additional field wiring information.

## Slide 6
Air Handling Unit:
Condenser:
Pairing 4 (Zone Sensor)
Odyssey Constant Volume AHU with ReliaTel Condenser
Trane Odyssey
Constant Speed Fan
Trane ReliaTel
1
2
Zone sensor wire – Up to 7 conductors may be required depending on the specific sensor used.
1
Thermostat wire – 6 conductors. REQUIRED for this pairing scenario.
RTRM
ReliaTel
Terminal
Strip
LTB1
B1
R
CD
H1
H2
EF
Control Wiring
5
4
3
2
1
2
Zone Sensor Wiring
Zone
Common
Cool Setpt
Mode
Heat Setpt
Zone Sensor
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
Notes: For pairing 4, the heating and cooling control is provided by the ReliaTel controller. Wire the zone sensor to the proper terminals on the Trane ReliaTel controller in the condenser. Use separate control wiring between the condenser and Trane Odyssey air handler. Depending on the exact features of the air handler and condenser pairing, the number of conductors needed for that control wire may vary. Refer to the wiring diagrams in the installation guide SS-SVN016* for additional field wiring information.

## Slide 7
Air Handling Unit:
Condenser:
Pairing E or F (Thermostat)
Odyssey Two-Speed/SZVAV AHU with ReliaTel Condenser
Trane Odyssey
Two-Speed/SZVAV
Trane ReliaTel
TR150
VFD
(SZVAV only)
2
Thermostat wire – 7 conductors. REQUIRED for this pairing scenario.
1
Thermostat wire – 6 conductors. REQUIRED for this pairing scenario.
RTRM
Terminal
Strip
LTB1
B1
R
CD
H1
H2
EF
Y2
COM
T
X2
W2
G
W1/O
Y1
R
ReliaTel
Thermostat
1
2
Thermostat Wiring
Control Wiring
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
Notes: For pairings E and F, the heating and cooling control is provided by the thermostat. Wire the thermostat to the RTRM controller in the Trane ReliaTel condenser. Use separate control wiring between the condenser and Trane Odyssey air handler. Depending on the exact features of the air handler and condenser pairing, the number of conductors needed for that control wire may vary. The VFD in the air handler is factory wired to the relay board and requires no field wiring. Refer to the wiring diagrams in the installation guide SS-SVN016* for additional field wiring information.

## Slide 8
Air Handling Unit:
Condenser:
Pairing E or F (Zone Sensor)
Odyssey Two-Speed/SZVAV AHU with ReliaTel Condenser
Trane Odyssey
Two-Speed/SZVAV
Trane ReliaTel
TR150
VFD
(SZVAV only)
2
Zone sensor wire – Up to 7 conductors may be required depending on the specific sensor used.
1
Thermostat wire – 6 conductors. REQUIRED for this pairing scenario.
RTRM
Terminal
Strip
LTB1
B1
R
CD
H1
H2
EF
ReliaTel
1
Control Wiring
2
5
4
3
2
1
Zone Sensor Wiring
Zone
Common
Cool Setpt
Mode
Heat Setpt
Zone Sensor
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
Notes: For pairings E and F, the heating and cooling control is provided by the ReliaTel controller. Wire the zone sensor to the proper terminals on the Trane ReliaTel controller in the condenser. Use separate control wiring between the condenser and Trane Odyssey air handler. Depending on the exact features of the air handler and condenser pairing, the number of conductors needed for that control wire may vary. The VFD in the air handler is factory wired to the relay board and requires no field wiring. Refer to the wiring diagrams in the installation guide SS-SVN016* for additional field wiring information.

## Slide 9
Air Handling Unit:
Pairing B (BACnet MS/TP, Thermostat)
Odyssey SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane Odyssey
SZVAV
[Digit 15 = D]
Trane Odyssey
Symbio 700
2
Thermostat wire – At least 4 conductors. REQUIRED for this pairing scenario.
3
Twisted-pair communication cable. Required only for Electric Heat, SZVAV applications. Proprietary comm.
1
Twisted pair communication cable. Required only for SZVAV applications. Modbus comm.
4
BACnet/BMS
5
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
5
TR150
VFD
(SZVAV only)
6
Thermostat wire – Up to 7 conductors
4
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
1
2
3
Communication (Modbus)
Communication (Proprietary)
Control Wiring
Thermostat
6
Thermostat Wiring
Condenser:
BMS communication requires the advanced controller
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
Notes: For pairings A and B, the heating and cooling control is this specific scenario is provided by the thermostat connected to the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane Odyssey air handler. Up to two additional communication cables are needed for electric heat applications or for SZVAV applications with a VFD. Those two communication cables must be twisted-pair cables, not thermostat wire. Lastly, for BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 10
Air Handling Unit:
Pairing A (BACnet MS/TP, Thermostat)
Odyssey Constant Volume with Odyssey/Symbio 700 Condenser
Trane Odyssey
Constant Volume
[Digit 15 = 1]
Trane Odyssey
Symbio 700
3
BACnet/BMS
4
2
Twisted-pair communication cable. Required only for Electric Heat applications. Proprietary comm.
3
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
1
Thermostat wire – At least 4 conductors. REQUIRED for this pairing scenario.
Thermostat wire – Up to 7 conductors
5
4
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
(* Second twisted pair not required for the last controller on the daisy-chain link)
1
2
Communication (Proprietary)
Control Wiring
Thermostat
5
Thermostat Wiring
Condenser:
BMS communication requires the advanced controller
IMC
*
* Options Module required for electric heat and heat pump applications.
Notes: For pairings A and B, the heating and cooling control is this specific scenario is provided by the thermostat connected to the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane Odyssey air handler. Up to two additional communication cables are needed for electric heat applications or for SZVAV applications with a VFD. Those two communication cables must be twisted-pair cables, not thermostat wire. Lastly, for BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 11
Air Handling Unit:
Pairing A or B (BACnet MS/TP, Thermostat)
Odyssey Constant Volume or SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane Odyssey
Constant Volume
or SZVAV
[Digit 15 = D]
Trane Odyssey
Symbio 700
4
BACnet/BMS
5
TR150
VFD
(SZVAV only)
2
Thermostat wire – At least 4 conductors. REQUIRED for this pairing scenario.
3
Twisted-pair communication cable. Required only for Electric Heat, SZVAV applications. Proprietary comm.
1
Twisted pair communication cable. Required only for SZVAV applications. Modbus comm.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
5
6
Thermostat wire – Up to 7 conductors
4
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
1
2
3
Communication (Modbus)
Communication (Proprietary)
Control Wiring
Thermostat
6
Thermostat Wiring
Condenser:
BMS communication requires the advanced controller
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
Notes: For pairings A and B, the heating and cooling control is this specific scenario is provided by the thermostat connected to the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane Odyssey air handler. Up to two additional communication cables are needed for electric heat applications or for SZVAV applications with a VFD. Those two communication cables must be twisted-pair cables, not thermostat wire. Lastly, for BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 12
Air Handling Unit:
Pairing A or B (BACnet MS/TP, Zone Sensor)
Odyssey Constant Volume or SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane Odyssey
Constant Volume or SZVAV
Trane Odyssey
Symbio 700
4
BACnet/BMS
5
TR150
VFD
(SZVAV only)
2
Thermostat wire – At least 4 conductors. REQUIRED for this pairing scenario.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
5
6
Zone sensor wire – Up to 7 conductors may be required depending on the specific sensor used.
4
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
Condenser:
6
Zone Sensor Wiring
Zone
Common
Cool Setpt
Mode
Heat Setpt
Zone Sensor
BMS communication requires the advanced controller
1
2
Modbus
Control Wiring
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
1
Twisted pair communication cable. Required only for SZVAV applications. Modbus comm.
3
Twisted-pair communication cable. Required only for Electric Heat, SZVAV applications. Proprietary comm.
3
Communication (Proprietary)
Notes: For pairings A and B, the heating and cooling control in this scenario is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane Odyssey air handler. Up to two additional communication cables are needed for electric heat applications or for SZVAV applications with a VFD. Those two communication cables must be twisted-pair cables, not thermostat wire. Lastly, for BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 13
Air Handling Unit:
Pairing A or B (Air-Fi Wireless)
Odyssey Constant Volume or SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane Odyssey
Constant Volume or SZVAV
Trane Odyssey
Symbio 700
Air-Fi Wireless Space Sensor
2
Thermostat wire – At least 4 conductors. REQUIRED for this pairing scenario.
TR150
VFD
(SZVAV only)
Condenser:
Air-Fi Wireless WCI
1
2
Communication (Modbus)
Control Wiring
BMS communication requires the advanced controller
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
1
Twisted pair communication cable. Required only for SZVAV applications. Modbus comm.
3
Twisted-pair communication cable. Required only for Electric Heat, SZVAV applications. Proprietary comm.
3
Communication (Proprietary)
Notes: For pairings A and B, the heating and cooling control in this scenario is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane Odyssey air handler. Up to two additional communication cables are needed for electric heat applications or for SZVAV applications with a VFD. Those two communication cables must be twisted-pair cables, not thermostat wire. Lastly, for Air-Fi Wireless communication to the Symbio 700 controller, The wiring harness provided with the WCI is sufficient for most installations of this pairing scenario. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 14
Air Handling Unit:
Pairing H (BACnet MS/TP, Thermostat)
Odyssey Two-Speed AHU with Odyssey/Symbio 700 Condenser
Trane Odyssey
Two-Speed Fan
Trane Odyssey
Symbio 700
1
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
4
Thermostat wire – 7 conductors
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
3
2
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
2
BACnet/BMS
3
1
Control Wiring
Thermostat
4
Thermostat Wiring
Condenser:
BMS communication requires the advanced controller
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
Notes: For pairing H, the heating and cooling control is provided by the thermostat connected to the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane Odyssey 2-speed air handler. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 15
Zone
Common
Cool Setpt
Mode
Heat Setpt
Zone Sensor
Air Handling Unit:
Pairing H (BACnet MS/TP, Zone Sensor)
Odyssey Two-Speed AHU with Odyssey/Symbio 700 Condenser
Trane Odyssey
Two-Speed Fan
Trane Odyssey
Symbio 700
2
BACnet/BMS
3
1
Control Wiring
Condenser:
4
Zone Sensor Wiring
BMS communication requires the advanced controller
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
1
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
4
Zone sensor wire – Up to 7 conductors may be required depending on the specific sensor used.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
3
2
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
5
Twisted-pair communication cable. Required only for Electric Heat, SZVAV applications. Proprietary comm.
IMC
5
Communication (Proprietary)
*
Notes: For pairing H, the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane Odyssey 2-speed air handler. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 16
Air Handling Unit:
Pairing H (Air-Fi Wireless)
Odyssey Two-Speed AHU with Odyssey/Symbio 700 Condenser
Trane Odyssey
Two-Speed Fan
Trane Odyssey
Symbio 700
Condenser:
2
Control Wiring
Air-Fi Wireless Space Sensor
Air-Fi Wireless WCI
2
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
1
Twisted pair communication cable. Required only for SZVAV applications with VFD. Proprietary comm.
BMS communication requires the advanced controller
IMC
*
* Options Module required for electric heat, SZVAV, and heat pump applications.
1
Communication (Proprietary)
Notes: For pairing H, the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane Odyssey 2-speed air handler. Lastly, for Air-Fi Wireless communication to the Symbio 700 controller, The wiring harness provided with the WCI is sufficient for most installations of this pairing scenario. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 17
Air Handling Unit:
Condenser Cooling Thermostat Wiring
Odyssey 2-Speed AHU with Odyssey/Symbio 700 Condenser
Trane Odyssey
Symbio 700
Thermostat
Condenser:
* Options Module required for electric heat and heat pump applications.
R-410A
2
Thermostat wire – Up to 7 conductors.
1
Thermostat wire – Up to 7 conductors
2
Control Wiring
1
Thermostat Wiring
IMC
Trane Odyssey
Two-Speed Fan
*
Notes: For the standard cooling only thermostat only scenario, the heating and cooling control is provided by the thermostat. A single control cable is required between the Odyssey condenser and Trane Odyssey 2-speed air handler.
The Symbio 700 controller accepts Y1 and Y2 inputs as requests for each compressor cooling stage.

## Slide 18
Air Handling Unit:
Heat Pump Thermostat Wiring
Odyssey 2-Speed AHU with Odyssey/Symbio 700 Heat Pump Condenser
Trane Odyssey
Symbio 700 Heat Pump
Thermostat
Condenser:
R-410A
2
Thermostat wire – Up to 8 conductors.
1
Thermostat wire – Up to 7 conductors
2
Control Wiring
1
Thermostat Wiring
Trane Odyssey
Two-Speed Fan
* Options Module required for electric heat and heat pump applications.
*
IMC
Notes: For the standard heat pump thermostat scenario, the heating and cooling control is provided by the thermostat. A single control cable is required between the Odyssey condenser and Trane Odyssey 2-speed air handler.
The Symbio 700 controller accepts Y1 and Y2 inputs as requests for each compressor cooling stage and the O input for the heat pump reversing valve.
Note: Electric heat is not available in the condenser heat pump defrost mode.

## Slide 19
Air Handling Unit:
Pairing 1 or 2 (BACnet MS/TP, Thermostat)
Electromechanical Constant Volume AHU with Odyssey/Symbio 700 Condenser
Electromechanical
Constant Volume
Trane Odyssey
Symbio 700
1
Thermostat wire – At least 6 conductors. REQUIRED for this pairing scenario.
4
Thermostat wire – 7 conductors. REQUIRED in all cases.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
3
2
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
2
BACnet/BMS
3
Terminal
Strip
LTB2
W1
W2
J
G
Y1
Y2
B1
R
B2
Thermostat
4
Thermostat Wiring
1
Control Wiring
Condenser:
BMS communication requires the advanced controller
Notes: For pairings 1 and 2, the heating and cooling control is normally provided by the thermostat connected to the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and electromechanical air handler. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 20
Air Handling Unit:
Pairing 1 or 2 (BACnet MS/TP, Zone Sensor)
Electromechanical Constant Volume AHU with Odyssey/Symbio 700 Condenser
Electromechanical
Constant Volume
Trane Odyssey
Symbio 700
1
Thermostat wire – At least 6 conductors. REQUIRED for this pairing scenario.
4
Zone sensor wire – Up to 7 conductors may be required depending on the specific sensor used.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
3
2
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
2
BACnet/BMS
3
Terminal
Strip
LTB2
W1
W2
J
G
Y1
Y2
B1
R
B2
Condenser:
1
Control Wiring
4
Zone Sensor Wiring
Zone
Common
Cool Setpt
Mode
Heat Setpt
Zone Sensor
BMS communication requires the advanced controller
Zone sensors not supported in this application; use thermostat instead
Notes: For pairings 1 and 2, the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and electromechanical air handler. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 21
Air Handling Unit:
Pairing 1 or 2 (Air-Fi Wireless)
Electromechanical Constant Volume AHU with Odyssey/Symbio 700 Condenser
Electromechanical
Constant Volume
Trane Odyssey
Symbio 700
1
Thermostat wire – At least 6 conductors. REQUIRED for this pairing scenario.
2
3
Condenser:
Twisted pair communication cable. Required only for Air-Fi Wireless in this pairing scenario.
3
2
Thermostat wire – At least 2 conductors. REQUIRED for this pairing scenario and Air-Fi Wireless.
Air-Fi Wireless Space Sensor
Air-Fi Wireless WCI
1
Air-Fi WCI
Terminal
Strip
LTB2
W1
W2
J
G
Y1
Y2
B1
R
B2
Control Wiring
BMS communication requires the advanced controller
Zone sensors not supported in this application; use thermostat instead
Notes: For pairings 1 and 2, the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and electromechanical air handler. For Air-Fi Wireless communication, two additional communication cables are needed. Use a two-conductor thermostat wire for the 24v power connection and a twisted pair for the IMC communication between the WCI and adapter board. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 22
Air Handling Unit:
Pairing G Option 1 (BACnet MS/TP, Thermostat)
ReliaTel SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane ReliaTel
SZVAV
Trane Odyssey
Symbio 700
1
Communication (Modbus)
TR150
VFD
2
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
5
Thermostat wire – 7 conductors. REQUIRED in all cases.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
4
3
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
1
Twisted pair communication cable. Required for SZVAV/VFD in this pairing scenario. Modbus comm.
3
BACnet/BMS
4
2
Terminal
Strip
LTB2
W1
W2
J
G
Y1
Y2
B1
R
B2
CD
EDC
Electric
Heat
Accessory
68
69
Control Wiring
Thermostat
5
Thermostat Wiring
Condenser:
BMS communication requires the advanced controller
50
53
Notes: For pairing G (preferred), the heating and cooling control is normally provided by the thermostat connected to the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane ReliaTel SZVAV air handler. An additional communication cable is required between the adapter board in the condenser and VFD in the air handler. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 23
Air Handling Unit:
Pairing G Option 1 (BACnet MS/TP, Zone Sensor)
ReliaTel SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane ReliaTel
SZVAV
Trane Odyssey
Symbio 700
1
2
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
Condenser:
5
Zone sensor wire – Up to 7 conductors may be required depending on the specific sensor used.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
4
3
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
Modbus
TR150
VFD
(SZVAV only)
1
Twisted pair communication cable. Required for SZVAV/VFD in this pairing scenario.
3
BACnet/BMS
4
2
Terminal
Strip
LTB2
W1
W2
J
G
Y1
Y2
B1
R
B2
CD
EDC
Electric
Heat
Accessory
68
69
Control Wiring
5
Zone Sensor Wiring
Zone
Common
Cool Setpt
Mode
Heat Setpt
Zone Sensor
BMS communication requires the advanced controller
Zone sensors not supported in this application; use thermostat instead
Notes: For pairing G (preferred), the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane ReliaTel SZVAV air handler. An additional communication cable is required between the adapter board in the condenser and VFD in the air handler. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 24
Air Handling Unit:
Pairing G Option 1 (Air-Fi Wireless)
ReliaTel SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane ReliaTel
SZVAV
Trane Odyssey
Symbio 700
2
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
3
4
Condenser:
Twisted pair communication cable. Required only for Air-Fi Wireless in this pairing scenario.
4
3
Thermostat wire – At least 2 conductors. REQUIRED for this pairing scenario and Air-Fi Wireless.
1
Twisted pair communication cable. Required for SZVAV/VFD in this pairing scenario.
Air-Fi Wireless Space Sensor
Air-Fi Wireless WCI
1
Modbus
TR150
VFD
(SZVAV only)
Terminal
Strip
LTB2
W1
W2
J
G
Y1
Y2
B1
R
B2
CD
EDC
Electric
Heat
Accessory
68
69
2
Control Wiring
Air-Fi WCI
BMS communication requires the advanced controller
Zone sensors not supported in this application; use thermostat instead
Notes: For pairing G (preferred), the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane ReliaTel SZVAV air handler. An additional communication cable is required between the adapter board in the condenser and VFD in the air handler. For Air-Fi Wireless communication, two additional communication cables are needed. Use a two-conductor thermostat wire for the 24v power connection and a twisted pair for the IMC communication between the WCI and adapter board. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 25
Air Handling Unit:
Pairing G Option 2 (BACnet MS/TP, Thermostat)
ReliaTel Two-Speed SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane ReliaTel
Two-Speed SZVAV
1
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
4
Thermostat wire – 7 conductors. REQUIRED in all cases.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
3
2
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
TR150
VFD
(SZVAV only)
2
BACnet/BMS
3
Terminal
Strip
LTB2
W1
W2
J
G
Y1
Y2
B1
R
B2
CD
Trane Odyssey
Symbio 700
Control Wiring
1
Thermostat
4
Thermostat Wiring
Condenser:
BMS communication requires the advanced controller
Notes: For pairing G (optional), the heating and cooling control is normally provided by the thermostat connected to the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane ReliaTel two-speed SZVAV air handler. For this application, the relay board is field applied in the existing air handler and wired to the Symbio 700 and associated adapter board in the condenser. No additional field wiring is needed for the VFD in the air handler. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 26
Air Handling Unit:
Pairing G Option 2 (BACnet MS/TP, Zone Sensor)
ReliaTel Two-Speed SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane ReliaTel
Two-Speed SZVAV
1
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
4
Zone sensor wire – Up to 7 conductors may be required depending on the specific sensor used.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
3
2
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
TR150
VFD
(SZVAV only)
2
BACnet/BMS
3
Terminal
Strip
LTB2
W1
W2
J
G
Y1
Y2
B1
R
B2
CD
Trane Odyssey
Symbio 700
Control Wiring
1
Condenser:
4
Zone Sensor Wiring
Zone
Common
Cool Setpt
Mode
Heat Setpt
Zone Sensor
BMS communication requires the advanced controller
Zone sensors not supported in this application; use thermostat instead
Notes: For pairing G (optional), the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane ReliaTel two-speed SZVAV air handler. For this application, the relay board is field applied in the existing air handler and wired to the Symbio 700 and associated adapter board in the condenser. No additional field wiring is needed for the VFD in the air handler. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 27
Air Handling Unit:
Pairing G Option 2 (Air-Fi Wireless)
ReliaTel Two-Speed SZVAV AHU with Odyssey/Symbio 700 Condenser
Trane ReliaTel
Two-Speed SZVAV
Trane Odyssey
Symbio 700
2
3
Condenser:
TR150
VFD
(SZVAV only)
Air-Fi Wireless Space Sensor
Air-Fi Wireless WCI
1
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
Twisted pair communication cable. Required only for Air-Fi Wireless in this pairing scenario.
3
2
Thermostat wire – At least 2 conductors. REQUIRED for this pairing scenario and Air-Fi Wireless.
Terminal
Strip
LTB2
W1
W2
J
G
Y1
Y2
B1
R
B2
CD
Control Wiring
1
Air-Fi WCI
BMS communication requires the advanced controller
Zone sensors not supported in this application; use thermostat instead
Notes: For pairing G (optional), the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and Trane ReliaTel two-speed SZVAV air handler. For this application, the relay board is field applied in the existing air handler and wired to the Symbio 700 and associated adapter board in the condenser. No additional field wiring is needed for the VFD in the air handler. For Air-Fi Wireless communication, two additional communication cables are needed. Use a two-conductor thermostat wire for the 24v power connection and a twisted pair for the IMC communication between the WCI and adapter board. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 28
Air Handling Unit:
Pairing Y (BACnet MS/TP, Thermostat)
Constant Volume AHU (By Others) with Odyssey/Symbio 700 Condenser
Generic AHU
Constant Volume
Trane Odyssey
Symbio 700
2
Thermostat wire – At least 4 conductors. REQUIRED for this pairing scenario.
4
Thermostat wire – 7 conductors. REQUIRED in all cases.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
4
3
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
1
2
BACnet/BMS
3
Terminal
Strip
W1
W2
G
Y1
Y2
B1
R
SH
Thermostat
Thermostat Wiring
Control Wiring
1
Condenser:
BMS communication requires the advanced controller
Notes: For pairing Y, the heating and cooling control is normally provided by the thermostat connected to the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and generic constant volume air handler. For this application, the terminal strip in the existing air handler is wired to the Symbio 700 and associated adapter board in the Trane Odyssey condenser. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 29
Air Handling Unit:
Pairing __ (BACnet MS/TP, Symbio 500 AHU)
Constant Volume AHU (Symbio 500) with Odyssey/Symbio 700 Condenser
Symbio 500 AHU
Constant Volume
Trane Odyssey
Symbio 700
2
Thermostat wire – Up to 7 conductors depending on the application.
Twisted pair communication cable(s) [daisy-chained].*
3
Twisted pair communication cable(s) [daisy-chained].
(* Second twisted pair not required for the last controller on the daisy-chain link)
1
2
BACnet MS/TP
3
Control Wiring
1
BMS communication requires the advanced controller
BACnet MS/TP
BACnet MS/TP
Condenser:
Notes: This pairing has not yet been assigned a pairing identification number. In this pairing the DX air handling unit is controlled with a Symbio 500 controller. Legacy AHUs may have also included either a Trane UC400 or UC600 controller, with similar connections. For this application, the Symbio 500 controller in the AHU is acting as the “thermostat” for the control of the Symbio 700 condenser. The outputs of the Symbio 500 in the AHU are directly wired to the thermostat inputs of the Symbio 700 in the condenser. The addition of BACnet communication to the Symbio 700 controller allows the BMS to view the pertinent status points. The Symbio 500 AHU controller in this example is applied with the Rooftop Unit / Heat Pump (RTU/HP) pre-packaged solution (PPS) programs.

## Slide 30
Air Handling Unit:
Pairing __ (BACnet MS/TP, Symbio 500 AHU)
Symbio 500 AHU with Odyssey/Symbio 700 Condenser
Symbio 500 AHU
Trane Odyssey
Symbio 700
2
Thermostat wire – Up to 3 conductors depending on the application.
Twisted pair communication cable(s) [daisy-chained].*
3
Twisted pair communication cable(s) [daisy-chained].
(* Second twisted pair not required for the last controller on the daisy-chain link)
1
2
BACnet MS/TP
3
Control Wiring
1
BMS communication requires
the advanced Symbio 700 controller
BACnet MS/TP
BACnet MS/TP
Condenser:
Notes: This pairing has not yet been assigned a pairing identification number. In this pairing the DX air handling unit is controlled with a Symbio 500 controller. Legacy AHUs may have also included either a Trane UC400 or UC600 controller, with similar connections. For this application, the Symbio 500 controller in the AHU is acting as the “thermostat” for the control of the Symbio 700 condenser. The outputs of the Symbio 500 in the AHU are directly wired to the thermostat inputs of the Symbio 700 in the condenser. The addition of BACnet communication to the Symbio 700 controller allows the BMS to view the pertinent status points. The Symbio 500 AHU controller in this example is applied with the Rooftop Unit / Heat Pump (RTU/HP) pre-packaged solution (PPS) programs.

## Slide 31
Air Handling Unit:
Pairing Y (BACnet MS/TP, Zone Sensor)
Constant Volume AHU (By Others) with Odyssey/Symbio 700 Condenser
Generic AHU
Constant Volume
Trane Odyssey
Symbio 700
2
Thermostat wire – At least 4 conductors. REQUIRED for this pairing scenario.
Zone sensor wire – Up to 7 conductors may be required depending on the specific sensor used.
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.*
4
3
Twisted pair communication cable(s) [daisy-chained]. Required only for BACnet MS/TP to BMS.
(* Second twisted pair not required for the last controller on the daisy-chain link)
1
2
BACnet/BMS
3
Terminal
Strip
W1
W2
G
Y1
Y2
B1
R
SH
Control Wiring
1
Condenser:
4
Zone Sensor Wiring
Zone
Common
Cool Setpt
Mode
Heat Setpt
Zone Sensor
BMS communication requires the advanced controller
Zone sensors not supported in this application; use thermostat instead
Notes: For pairing Y, the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and generic constant volume air handler. For this application, the terminal strip in the existing air handler is wired to the Symbio 700 and associated adapter board in the Trane Odyssey condenser. For BACnet MS/TP communication to the Symbio 700 controller, two additional communication cables are needed to complete the daisy-chain connection to and from the controller, unless the unit is at the end of the communication link, in which case only one communication cable is needed. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 32
Air Handling Unit:
Pairing Y (Air-Fi Wireless)
Constant Volume AHU (By Others) with Odyssey/Symbio 700 Condenser
Generic AHU
Constant Volume
Trane Odyssey
Symbio 700
Condenser:
2
3
Air-Fi Wireless Space Sensor
Air-Fi Wireless WCI
1
Thermostat wire – At least 7 conductors. REQUIRED for this pairing scenario.
Twisted pair communication cable. Required only for Air-Fi Wireless in this pairing scenario.
3
2
Thermostat wire – At least 2 conductors. REQUIRED for this pairing scenario and Air-Fi Wireless.
Terminal
Strip
W1
W2
G
Y1
Y2
B1
R
SH
Control Wiring
1
Air-Fi WCI
BMS communication requires the advanced controller
Zone sensors not supported in this application; use thermostat instead
Notes: For pairing Y, the heating and cooling control is normally provided by the Symbio 700 controller in the Trane Odyssey condenser. Separate control wiring is required between the condenser and generic constant volume air handler. For this application, the terminal strip in the existing air handler is wired to the Symbio 700 and associated adapter board in the Trane Odyssey condenser. For Air-Fi Wireless communication, two additional communication cables are needed. Use a two-conductor thermostat wire for the 24v power connection and a twisted pair for the IMC communication between the WCI and adapter board. For BACnet/IP, a single ethernet cable is used to connect the Symbio 700 to the network switch (BACnet/IP not shown).

## Slide 33
BACnet MS/TP
Air Handling Unit:
Condenser Control (Symbio 500, Zone Sensor)
Symbio 500 AHU with Odyssey/Symbio 700 Condenser
Symbio 500 AHU
Constant Volume
Trane Odyssey
Symbio 700
2
Thermostat wire – Up to 4 conductors.
1
Thermostat wire – Up to 3 conductors
1
2
Control Wiring
Zone Sensor Wiring
Condenser:
Zone
Common
Cool Setpt
Mode
Heat Setpt
Zone Sensor
Notes: Questions:
Does this scenario also support 2-speed fan operation?
Can the power and common wires be moved from the Adapter Board to the Symbio 700?
Should we show heat pump details on this slide or dedicate another slide to that application?

## Slide 34
Air Handling Unit:
Condenser Control (Symbio 500, Air-Fi)
Symbio 500 AHU with Odyssey/Symbio 700 Condenser
Symbio 500 AHU
Constant Volume
Trane Odyssey
Symbio 700
1
Thermostat wire – Up to 4 conductors
1
Control Wiring
Condenser:
Air-Fi Wireless Space Sensor
Air-Fi Wireless WCI
Notes: Questions:
Does this scenario also support 2-speed fan operation?
Can the power and common wires be moved from the Adapter Board to the Symbio 700?
Should we show heat pump details on this slide or dedicate another slide to that application?